## Slide 1: Basic Electricity
Date
Time
Presented by

## Slide 2: A Little History
1800 Volta
  First electric battery
1802
  Electric Arc Lamp invented
1830-31 Faraday and Henry
  Changing magnetic field can induce an electric current. Build first very crude electric motors in lab.
1832 Pixii
  First crude generation of an AC current.
1856 Siemens
  First really practical electric motor
1860s Varley, Siemens and Wheatstone
  Each develop electric dynamos (DC Generators).

## Slide 3: Electricity Starts to Take Off
1870s
  First electric railroad and street lights in Berlin (DC).
1879 Edison
  Incandescent light bulb
1880
  First electric elevator (DC).
1885-88 Thomson, Ferraris, Tesla
  Each develop AC electric induction motors.
  Tesla is granted a US patent for induction motor in 1888.
1890 Dolivo-Dobrovolsky
  First three phase generator, motor and transformer

## Slide 4: AC vs DC
Direct Current (DC) – an electric current that flows in one direction.(IEEE100)
Alternating Current (AC) – an electric current that reverses direction at regularly recurring intervals of time. (IEEE100)

## Slide 5: AC vs DC
Edison and Westinghouse
  Edison favored DC power distribution, Westinghouse championed AC distribution.
  The first US commercial electric systems were Edison’s DC systems.
First AC system was in 1893 in Redlands, CA. Developed by Almirian Decker it used 10,000 volt, three phase primary distribution.
Siemens, Gauland and Steinmetz were other pioneers.

## Slide 6: War of the Currents
Thomas Edison
George Westinghouse
Nikola Tesla

## Slide 7: The Problem with Direct Current
High losses required generators to be near the loads – maximum of one mile without huge conductors
Difficult to change voltages for transmission with DC

## Slide 8: 1888: A Young Serb Named Никола Тесла (Nicola Tesla) Meets George Westinghouse
Nicola Tesla, "The Wizard of The West"
1893: World’s Fair Chicago lighted by Westinghouse / Tesla
1882: Induction Motor
1888: Westinghouse, American entrepreneur and engineer meets Tesla

## Slide 9: 1893: Westinghouse Awarded the Contract for Powerhouse at Niagara Falls
Edward Dean Adams power station at Niagara, with ten 5,000-horsepower Tesla/Westinghouse AC generators — the culmination of Tesla's dream. (Courtesy Smithsonian Institution)

## Slide 10: AC Theory - History
By 1900 AC power systems had won the battle for power distribution.
  Transformers allowed more efficient distribution of power over large areas.
  AC motors were cheaper and easier to build.
  AC electric generators were easier to build.

## Slide 11: AC Circuits
An AC circuit has three general characteristics
  Voltage
  Frequency
  Phase
In the US, the household value is 120 Volts with other common voltages being 208, 240, 277 and 480 Volts. The frequency is 60 Hertz (cycles per second).

## Slide 12: Some Background
The Atom
  All matter is made up of atoms.
  Atoms are composed of three particles
    Protons – with a positive charge
    Electrons – with a negative charge
    Neutrons – with no charge
Each atom has the same number of protons and electrons. That number is called the atomic number of the atom and determines the element.
For example: If the atomic number is 8 as shown in the figure to the left the element is Oxygen (O).

## Slide 13: Some Background
Charge
  Opposite charges attract each other.
  That is what holds the electrons of an atom to the protons of the nucleus.
  Like charges repel each other.

## Slide 14: Man “Discovers” Electricity
Static Electricity
  Awareness of a “strange force” goes back to the beginning of recorded history. Early man realized that rubbing a piece of amber with an animal skin imparted some mystical property to the amber.
    It would attract hair and small bits of debris.
    We get the same effect when we rub a balloon on a fur or cloth

## Slide 15: Man “Discovers” Electricity
Static Electricity
  What is this strange force? “Static” electricity.
    Rubbing the cloth across an insulator causes electrons to move from one object to the other. This leaves one object with more electrons than it should have and the other with less. The cloth has less so it becomes positively charged.

## Slide 16: “Dynamic” Electricity
Current – Electrons flowing from one place to another
  If one object has a negative charge and another has a positive charge Electrons will flow from the negative to the positive if they are connected

## Slide 17: Practical Electricity
Direct Current – DC
  In our “zap” electrons briefly travelled from the negative object to the positive object.
    Until the excess electrons ran out the current flowed.
    Once they ran out the current stopped.
  A battery is a device that continuously supplies electrons through a chemical reaction.
    Hook the positive side of a battery through a load to the negative side and electrons will flow.
    This is a current (a flow of electrons)
    Since it goes in only one direction it is called DIRECT CURRENT

## Slide 18: Practical Electricity
Direct Current – DC
  Sources of direct current include
    Batteries – electrons are supplied by a chemical reaction
    Thermocouples – electrons are supplied by heat
    Photovoltaic cells – electrons are supplied by light
    Electronic Power Supplies – Generally transform AC electricity to DC electricity because electronic devices run off of DC electricity
  There always has to be some form of energy to produce the electrons for the current
  Modern electronic devices all run off of DC electricity

## Slide 19: DC Electricity
Basic Concepts
  Current – The flow of electrons
    The general convention is that a POSITIVE current is a current that flows from the positive terminal of the source to the negative terminal of the source
    Why – Electrons actually flow the other direction?
      Scientists made up the conventions long before they discovered electrons, they got it backwards and we still use the convention today.
  Voltage – A measure of the potential difference between two points
    Voltage is to current, as the pressure in a pipe is to the water
    The higher the voltage (potential difference), the easier it is for current to flow
  Impedance – Something which resists the flow of current.
    Resistor – The most common and simplest impedance
    Capacitor – An impedance which stores the electrons as they try to flow through
      Energy is stored in an electric field
    Inductor – An impedance which resists the change in current flowing through the device
      Energy is stored in a magnetic field

## Slide 20: Basic Electrical Units
Charge – Coulombs
  “Q” – 1 coulomb = 6.2415 x1018 electron charges
Current – Amperes
  “I or A” – 1 ampere = 1 coulomb per second of charge flow
Voltage – Volt
  “V or E” – The potential difference required to do 1 joule of work
Impedance – Resistance - Ohm
  “R” – Resistance
  Ohm’s Law - V = IR
  One volt applied across one ohm results in 1 ampere of current.

## Slide 21: Basic Electrical Units
Impedance – Capacitance - Farad
  “C” – Capacitance
Impedance – Inductance - Henry
  “L” – Inductance
Power – Watt
  A rate of energy consumption. A measure of work performed.
  For DC electricity = product of voltage and current
Energy – For Electricity – Watt-Hours (DC ONLY – AC IS MORE COMPLICATED)
  The energy when one ampere flows with a potential of one volt for one hour

## Slide 22: Basic Electrical Laws
Ohms Law
  Voltage = Current times Resistance
  V = I X R
  THE MOST USEFUL AND THE MOST FUNDAMENTAL OF THE ELECTRICAL LAWS

## Slide 23: Basic Concepts: Electricity and Water
Comparing Electricity to Water flowing from a hose
  Voltage is the equivalent of the pressure in the hose
  Current is water flowing through a hose (coulombs/sec vs gal/sec). The water in a system is the “charge” (coulombs)
  Impedance(Resistance) is the size of the hose. The nozzle would provide a change in resistance.
  Power is how fast water flows from a pipe (gallons per minute vs kilowatts). Power is a rate of energy consumption

## Slide 24: Basic Concepts: Electricity and Water

## Slide 25: Basic Concepts: Electricity and Water

## Slide 26: Practical Electricity

## Slide 27: Basic Electrical Laws
Ohms Law Examples
  If V = 20 volts and I = 5 amperes what is the resistance?
    R = V / I = 20 / 5 = 4 ohms
  If R = 20 ohms and V = 120 volts what is the current?
    I = V / R = 120 / 20 = 6 amps
  If I = 10 amperes and R = 24 ohms what is the voltage?
    V = I x R = 10 x 24 = 240 volts
  Problem: If V = 240 volts and R = 6 ohms what is the current?
    I = V / R = 240 / 6 = 40 amps

## Slide 28: Basic Electrical Laws

## Slide 29: Basic Electrical Laws
Power = Voltage x Current = V x I = I2R = V2/R
  If V = 20 volts and I = 8 amperes what is the power?
    P = V x I = 20 x 8 = 160 watts
  If R = 5 ohms and V = 120 volts what is the power?
    P = V2/R = 120 x 120 / 5 = 2880 watts
  If I = 10 amperes and R = 20 ohms what is the power?
    P = I2R = 10 x 10 x 20 = 2000 watts
    1 kilowatt (kW) = 1,000 watts
    1 megawatt (MW) = 1,000,000 watts

## Slide 30: Basic Electrical Laws
Kirchoff’s Voltage Law (KVL)
The sum of the voltages around a circuit loop is zero.
  V = V1 + V2 + V3 = I * (R1 + R2 + R3) = I1 * R1 + I2 * R2 + I3 * R3
  I = I1 = I2 = I3
Resistors in series add

## Slide 31: Basic Electrical Laws
Kirchoff’s Voltage Law (KVL) – PROBLEM #1
  I = V / R = V / (R1 + R2 + R3) = 120/(10+20+30) = 2 amperes
  V1 = I*R1 = 2 *10 = 20 volts
  V2 = I*R2 = 2 *20 = 40 volts
  V3 = I*R3 = 2 *30 = 60 volts
What is the current in the circuit?
What are V1, V2, V3?

## Slide 32: Basic Electrical Laws
Kirchoff’s Current Law (KCL)
The sum of the currents at a node in a circuit is zero.
  I = I1 + I2 + I3
  If Loads are placed in parallel they sum up.
  So does power
  P = V x I = V x I1 + V x I2 + V x I3

## Slide 33: Basic Electrical Laws

## Slide 34: Basic Electrical Laws
Compute
I1, I2, I3
I
R (parallel resistance of R1, R2, R3)
  I1 = 120/10 = 12A, I2=120/20=6A, I3=120/30= 4A
  I = 12 + 6 + 4 =22A
  R = V/I = 120 / 22 = 5.4545 ohms

## Slide 35: Basic Electrical Laws
Compute
I1, I2, I3
I
R (parallel resistance of R1, R2, R3)

## Slide 36: Basic Electrical Laws
Compute
R1, R2, R3
I
R (parallel resistance of R1, R2, R3)
  I = 10 + 20 + 5 =35A
  R = V/I = 240 / 35 = 6.857 ohms

## Slide 37: Basic Electrical Laws
More complex circuits
  V = V1 + V2
  I = I1 + I2 + I3

## Slide 38: Basic Electrical Laws
More complex circuits

## Slide 39: Basic Electrical Laws
More complex circuits

## Slide 40: Basic Electrical Laws
More complex circuits
Compute
V2
R1, R2, R3, R4
Total Power
V2 = 240 – 40 = 200 volts
R1 = 40/10 = 4, R2 = 200/5 = 40,
R3 = 200/3 = 66.667, R4 = 200/2 = 100

## Slide 41: Basic AC Theory Power – The Simple View
E = Voltage (rms)
I = Current (rms)
PF = Power Factor
Power = Watts = E x I x PF
Power is sometimes
referred to as Demand
Sinusoidal
Waveforms
Only
NO
Harmonics
For a 120 Volt service drawing
13 Amps at Unity (1.0) PF,
how much power is being drawn?
Power = 120 x 13 x 1.0 = 1560 Watts

## Slide 42: Basic Meter Math Power – The Simple View
For a 120 Volt service drawing
13 Amps at 0.866 PF,
how much power is being drawn?
Power = 120 x 13 x 0.866 = 1351 Watts
For a 480 Volt service drawing
156 Amps at 0.712 PF,
how much power is being drawn?
Power = 480 x 156 x 0.712 = 53,315 Watts

## Slide 43: Basic AC Theory Power – The Simple View
In the previous example we had:
Power = 480 x 156 x 0.712 = 53,315 Watts
Normally we don’t talk about Watts, we speak in Kilowatts
1000 Watts = 1 Kilowatt = 1 kW
Watts / 1000 = Kilowatts
For a 480 Volt service drawing
156 Amps at Unity (0.712) PF,
how many Kilowatts are being drawn?
Power = 480 x 156 x 0.712 / 1000 = 53.315 kW

## Slide 44: Basic AC Theory Energy – What We Sell
If power is how fast water flows from a pipe,
then energy is how much water we have in a bucket
after the water has been flowing for a specified time.
Energy = Power x Time
1 kW for 1 Hour = 1 Kilowatt-Hour = 1 kWh
Energy (Wh) = E x I x PF x T
where T = time in hours
Energy (kW) = (E x I x PF / 1000) x T

## Slide 45: Basic Meter Math Energy – What We Sell
For a 120 Volt service drawing 45 Amps at a Power Factor of 0.9 for 1 day,
how much Energy (kWh) has been used?
Energy = (120 x 45 x 0.9 / 1000) x 24 = 116.64 kWh
For a 240 Volt service drawing 60 Amps at a Power Factor of 1.0 for 5.5 hours,
how much Energy (kWh) has been used?
Energy = (240 x 60 x 1.0 / 1000) x 5.5 = 79.2 kWh

## Slide 46: Basic Meter Math Energy – What We Sell
For a 120 Volt service drawing 20 Amps at a Power Factor of 0.8 from 8:00AM to 6:00PM,
and 1 Amp at PF=1.0 from 6:00PM to 8:00AM
how much Energy (kWh) has been used?
8:00AM to 6:00PM = 10 hours
6:00PM to 8:00AM = 14 hours
Energy = (120 x 20 x 0.8 / 1000) x 10 = 19.2 kWh
Energy = (120 x 1 x 1 / 1000) x 14 = 1.68 kWh
Energy = 19.2 kWh + 1.68 kWh = 20.88 kWh

## Slide 47: Basic AC Theory What is VA?
Power was measured in Watts. Power does useful work. The power that does useful work is referred to as
“Active Power.”
VA is measured in Volt-Amperes. It is the capacity required to deliver the Power. It is also referred to as the “Apparent Power.”
Power Factor = Active Power / Apparent Power
VA = E x I
PF = W/VA

## Slide 48: Basic Meter Math Power – VA
For a 120 Volt service drawing 13 Amps at 0.866 PF
How much power is being drawn?
Power = 120 x 13 x 0.866 = 1351 Watts
How many VA are being drawn?
VA = 120 x 13 = 1560 Volt-Amperes

## Slide 49: Basic Meter Math Power – VA
For a 480 Volt service drawing 156 Amps at 0.712 PF
How much power is being drawn?
Power = 480 x 156 x 0.712 = 53,315 Watts
How many VA are being drawn?
VA = 480 x 156 = 74,880 Volt-Amperes

## Slide 50: Basic Meter Math Power – VA
For a 120 Volt service drawing 60 Amps at 1.00 PF
How much power is being drawn?
Power = 120 x 60 x 1.00 = 7,200 Watts
How many VA are being drawn?
VA = 120 x 60 = 7,200 Volt Amperes

## Slide 51: Basic AC Theory Sinusoidal Waveforms
Peak Value
RMS Value

## Slide 52: Basic AC Theory Power Factor = 1.0

## Slide 53: Basic AC Theory Instantaneous Power
P = 11520 Watts
Power is a “rate of flow” like water running through a pipe.
Average Power

## Slide 54: Basic AC Theory Instantaneous Power
Average Power
P = 9,976 Watts
PF=0.866

## Slide 55: Basic Meter Math What about polyphase systems?
Calculating power in a polyphase system is actually simple but sometimes we make it complex.
3 Phase, 4-Wire “Y” Service

## Slide 56: Basic Meter Math 3 Phase, 4-Wire “Y” Service
Va
Vb
Vc
The total power is equal to the sum of the power in each phase.
Ptotal = Ea x Ia x Cos(θa) + Eb x Ib x Cos(θb) + Ec x Ic x Cos(θc)
In a balanced system where Va = Vb = Vc and Ia = Ib = Icand θa = θa = θa
Ptotal = 3 x Ea x Ia x Cos(θa)

## Slide 57: Basic Meter Math 3 Phase, 4-Wire “Y” Service
For a balanced system
E = 277 V
I = 20 A
PF = 1.00
In a balanced system where Va = Vb = Vc and Ia = Ib = Ic and θa = θa = θa
Ptotal = 3 x Ea x Ia x Cos(θa) = 3 x Ea x Ia x PF
Ptotal = 3 x 277 x 20 x 1.0
Ptotal = 3 x 277 x 20 x 1.0 = 16,620 W

## Slide 58: Basic Meter Math 3 Phase, 4-Wire “Y” Service
For a unbalanced system
Ea = 284 V, Eb = 274 V, Ec = 276 V
Ia = 20 A, Ib = 32 A, Ic = 30 A
PFa = 0.900, PFb = 0.784, PFc = 0.866
The total power is equal to the sum of the power in each phase.
Ptotal = Pa + Pb + Pc
Ptotal = Ea x Ia x Cos(θa) + Eb x Ib x Cos(θb) + Ec x Ic x Cos(θc)
Pa = 284 x 20 x .900
= 5,112
Pb = 274 x 32 x .784
= 6,874
Pc = 276 x 30 x .866
= 7,170
Ptotal = 5,112 + 6,874 + 7,170 = 19,156

## Slide 59: Basic AC Theory What is VA?
If we were trying to decide how big the transformers in the last example need to be, we would need to calculate the kVA of the loads rather than the kW.
REMEMBER
VA is measured in Volt-Amperes. It is the capacity required to deliver the Power. It is also referred to as the “Apparent Power”.
VA = E x I
PF = W/VA

## Slide 60: Basic Meter Math 3 Phase, 4-Wire “Y” Service
What is the VA for each phase?
Ea = 284 V, Eb = 274 V, Ec = 276 V
Ia = 20 A, Ib = 32 A, Ic = 30 A
PFa = 0.900, PFb = 0.784, PFc = 0.866
The total power is equal to the sum of the power in each phase.
VAtotal = VAa + VAb + VAc
VAtotal = Ea x Ia + Eb x Ib + Ec x Ic
Pa = 284 x 20 = 5,680
Pb = 274 x 32 = 8,768
Pc = 276 x 30 = 8,280
Ptotal = 5,680 + 8,768 + 8,280 = 25,328
Would you use 5kVA, 7.5kVA, 10kVA, 25kVA or 40kVA transformers?

## Slide 61: Induction Meters
Using concepts put forth by Tesla and Ferraris, several inventors created early induction watthour meters
Two coils and a conducting (usually aluminum) disk. A braking magnet.
Magnetic field from the first coil generates eddy currents in the disk
Magnetic field from the second coil interacts with the eddy currents to cause motion
Disk would accelerate without bound except for eddy currents caused by motion through fixed magnetic field which slows the disk
The end result is that each revolution of the disk measures a constant amount of energy

## Slide 62: Basic Energy Formula
The essential specification of a watthour meter’s measurement is given by the value Kh [ Watthours per disk revolution ]
The watthour meter formula is as follows:

## Slide 63: 1893: Blondel’s Theorem
The theory of polyphase watthour metering was first set forth on a scientific basis in 1893 by Andre E. Blondel, engineer and mathematician. His theorem applies to the measurement of real power in a polyphase system of any number of wires. The theorem is as follows:
  - If energy is supplied to any system of conductors through N wires, the total power in the system is given by the algebraic sum of the readings of N wattmeters, so arranged that each of the N wires contains one current coil, the corresponding voltage coil being connected between that wire and some common point. If this common point is on one of the N wires, the measurement may be made by the use of N-1 wattmeters.

## Slide 64: Questions and Discussion
Mike Guilfolye Sr.
Electrical Engineering Manager
TESCO – The Eastern Specialty Company
Bristol, PA
215.228.0500
This presentation can also be found under Meter Conferences and Schools on the TESCO website: tescometering.com
ISO 9001:2015 Certified Quality Company
ISO 17025:2017 Accredited Laboratory