## Slide 1: High Accuracy Current Transformers
July 10, 2023
11:15 AM – 12:00 PM
Tom Lawton

## Slide 2: Where Would You Use High Accuracy CT’s?
Inside of…
Switchgear
Metering Panels
LV Switchgear, MCC’s
Installed at…
Generator
Transformers
Transformers

## Slide 3: Current Transformers
Secondary
(Output)
Primary
(Input)
Core
Transform the voltage or current input into a standard 5 or 1 amp output

## Slide 4
Accuracy – How close can you get it to the Gator Head.
Loser must retrieve balls.

## Slide 5: What Impacts Accuracy?
Number of Secondary Turns
Core material and/or cross section
Secondary Burden

## Slide 6: Energy Required to Energize the Core
Courtesy of Electric Power Transformer Handbook
Secondary turns or core cross section
secondary impedance
If
energy required to energize core
Then

## Slide 7
Graph: Bill Hardy – TESCO
Core energy needed
Saturation
tescometering.com
7

## Slide 8: CT Metering Accuracy
Actual secondary
current
Rated secondary
current
=
Difference in % is known as the “Accuracy”
of the CT
Definition: There are two sources of error in instrument transformers, namely ratio error and phase angle error. In a given transformer, the metering error is the combination of the two separate errors. This combination is called Transformer Correction Factor (TCF), IEEE has established accuracy classes for both current and potential transformers. The limit of permissible error in a potential transformer for a given accuracy class remains constant over a range of voltage from 10% below to 10% above rated voltage

## Slide 9: Ratio Correction Factor (RCF)
IEEE C57.13 Terminology
RCF = True Ratio / Marked Ratio
Example: 500:5 CT
By test, CT Ratio = 100.1
RCF = 100.1 / 100 = 1.0010
What does this mean? How many amps is the meter seeing?
A. – With 500A through primary, only 4.995A is flowing on the secondary 4.995 x 1.001 = 5A. (Negative current error due to losses)

## Slide 10: Ratio Correction Factor (RCF)
RCF on Knopp Comparator

## Slide 11: Phase Error
Red = Primary Current
Blue = Secondary Current
When Secondary Current (blue) leads the Primary Current (red), Phase Error () is defined as Positive.
Difference measured in minutes
1 minute = 0.77usec (60Hz)

## Slide 12
Phase Error on Knopp Comparator
Phase Error

## Slide 13: IEEE Std. C57.13 limits of accuracy class for current transformers for metering 0.3 accuracy class
Recall the Knopp Comparator
The values were:
Ratio Error = 1.00278
Φ Angle Error = 5.2
CT Parallelogram

## Slide 14: IEEE C57.13 – Accuracy Limits
Ratio Correction Factor (RCF)
Phase Angle, minutes
Lagging Leading
CT Parallelogram

## Slide 16: Standard 0.3 Accuracy Class
0.30
0.30
0.60
0.60
Rating Factor
Accuracy Class - %
10%
1.0
RF
IEEE C57.13 Accuracy
0.3 @ BX.X; RF = X.X
±0.3% Accuracy
from 100% rated current up to RF
100%
±0.6% Accuracy
from 10% to 100%
of rated current
No accuracy guaranteed at current levels less than 10%
Typical 0.3 CT Performance Curve

## Slide 17: ITI Encompass
0.30
0.30
0.60
0.60
Rating Factor
Accuracy Class - %
4%
100%
1.0
“Stretching” the rating factor
0.30 @ BX.X; RF 0.4-X.X
0.15
0.15
.4
40%
RF
±0.3% Accuracy
from 40% rated current up to RF
±0.6% Accuracy
from 4% to 40%
of rated current
Typical Encompass
Performance Curve

## Slide 18: 0.15 High Accuracy Class
0.30
0.30
0.60
0.60
Rating Factor
Accuracy Class - %
5%
1.0
±0.15% Accuracy
from 100% up to RF
100%
±0.3% Acc. from 5% - 100%
0.15
0.15
IEEE C57.13.6 Accuracy
0.15 @ BX.X; RF = X.X
Typical 0.15 CT Performance Curve
No accuracy guaranteed at current levels less than 5%
RF

## Slide 19: 0.15S Special High Accuracy (Accubute)
0.30
0.30
0.60
0.60
Rating Factor
Accuracy Class - %
100%
1.0
0.15
0.15
IEEE C57.13.6 Accuracy
0.15 @ E0.04, E0.20; 0.15 @ BX.X; RFX.X
5%
±0.15% Accuracy
from 5% up to RF
Typical CT Accubute™ Performance Curve
No accuracy guaranteed at current levels less than 5%
RF

## Slide 20: 0.15S High Accuracy Extended Range
0.30
0.30
0.60
0.60
Rating Factor
Accuracy Class - %
100%
1.0
0.15
0.15
1%
±0.15% Accuracy
from 5% up to RF
Typical CT Accubute™ Performance Curve
No accuracy guaranteed at current levels less than 1%
RF
“Stretching” the rating factor
0.15 @ BX.X; RF X.X

## Slide 21: Definitions
Standard Revenue Metering Accuracy (IEEE 0.3 Accuracy Class)
± 0.3% accurate from 100% Nameplate Rating, up to Rating Factor
± 0.6% accurate below 100% Nameplate Rating, down to 10% of Nameplate Rating
GE ITI Encompass CT’s
± 0.3% accurate from 40% of Nameplate Rating, up to Rating Factor
± 0.6% accurate below 40% Nameplate Rating down to 4% of Nameplate Rating
High Accuracy (IEEE 0.15 Accuracy Class)
± 0.15% accurate from 100% Nameplate Rating, up to Rating Factor
± 0.3% accurate below 100% Nameplate Rating, down to 5% of Nameplate Rating
GE Somersworth Accubute™ (IEEE 0.15S Accuracy Class)
± 0.15% accurate from down to 5% of Nameplate Rating, up to Rating Factor
GE RevenueSense High Accuracy Extended Range (IEEE 0.15S Accuracy Class)
± 0.15% accurate from down to 1% of Nameplate Rating, up to Rating Factor

## Slide 22: UTILITY METERING CTs
What do I need to know?
B - Burden
R - Ratio
A - Accuracy
V – voltage class
E – Etc (window size, special requirements)
R – Rating Factor
Revenue metering application

## Slide 23: Name Plate Information: Burden
Definition: Load connected to CT secondary
Includes devices & connecting leads
Expressed in ohms
Standard values = B0.1, B0.2, B0.5, B0.9, B1.8
E0.04, E0.2

## Slide 24: Standard CT Burdens
Standard IEEE CT Burdens (5 Amp) (Per IEEE Std. C57.13-1993 & C57.13.6)
E0.2
E0.04
0.2
0.04
5
1
1.0
1.0

## Slide 25: Standard Accuracy Extended Range

## Slide 26: Low Voltage Encompass™ Series
System Current | 20A | 40A | 60A | 80A | 100A | 200A | 400A | 600A | 800A | 1000A | 1200A | 1400A | 1600A | 1800A | 2000A
200:5 JAK-0C (Rating Factor 4.0) | ±0.6% Accuracy |  |  |  |  | ±0.3% Accuracy |  |  |  |  |  |  |  |  | 
400:5 JAK-0C (Rating Factor 4.0) |  | ±0.6% Accuracy _ |  |  |  |  | ±0.3% Accuracy |  |  |  |  |  |  |  | 
1000:5 JAK-0C (Rating Factor 2.0) |  |  |  |  | ±0.6% Accuracy |  |  |  |  | ±0.3% Accuracy |  |  |  |  | 
500:5 JAK-0W Encompass™ (4% to 400%) | ±0.6% Accuracy |  |  |  |  | ±0.3% Accuracy |  |  |  |  |  |  |  |  | 
One Encompass CT offers equal to, or better accuracy class
over the range of multiple legacy CT’s

## Slide 27: High Accuracy Extended Range

## Slide 28: Low Voltage RevenueSense™ Series
One RevenueSense™ CT improves accuracy over the range of multiple legacy CT’s, with significant improvement at low currents
System Current | 6A | 20A | 40A | 60A | 80A | 100A | 200A | 400A | 600A | 800A | 1000A | 1200A | 1400A | 1600A | 1800A | 2000A
200:5 JAK-0C (Rating Factor 4.0) |  | ±0.6% Accuracy |  |  |  |  | ±0.3% Accuracy |  |  |  |  |  |  |  |  | 
400:5 JAK-0C (Rating Factor 4.0) |  |  | ±0.6% Accuracy _ |  |  |  |  | ±0.3% Accuracy |  |  |  |  |  |  |  | 
1200:5 JAK-0C (Rating Factor 1.5) |  |  |  |  |  | ±0.6% Accuracy |  |  |  |  |  | ±0.3% Accuracy |  |  |  | 
600:5 JAK-0S High Revenue Sense (1% to 300%) | ±0.15% Accuracy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 

## Slide 29: Product Line Summary
Tip: To navigate between the first level copy and the first level bullet, use the Indent and Outdent button on the Home Ribbon.
Once you are on the second, and third level bullets, you can Tab and Shift-Tab to go back and forth between the bullet levels.

## Slide 30: Factors Influencing CT Accuracy
Physical Size
Current Ratio
Burden
“Large windows, small cross-section”
and “High accuracy” are not friends!!
“Low ratio” and “high accuracy” are not friends!!
“High burden” and “High Accuracy” are not friends!!
Notes: What affects accuracy??

## Slide 31: Sizing CTs for Metering
Use as low of a ratio as possible with the RF covering the maximum current level
CT error is almost always negative
Using a more accurate metering class will almost always result in higher revenue levels
Burden adversely affects accuracy, the lower the applied burden, the better the accuracy performance

## Slide 32
Questions and Discussion
Tom Lawton
President
TESCO – The Eastern Specialty Company
Bristol, PA
215.228.0500
This presentation can also be found under Meter Conferences and Schools on the TESCO website: tescometering.com
ISO 9001:2015 Certified Quality Company
ISO 17025:2017 Accredited Laboratory