## Slide 1: Testing CT’s and Meters in a Three Phase Installation
Track 2 Polyphase
Monday, July 10th, 2023
3:45-4:30pm
John Carroll
Notes: 1

## Slide 2: What we will cover
Why do we test CT’s?
Shop testing
How to read and interpret a transformer face plate
Types of field tests
Magnetization effects and demagnetization

## Slide 3: Shop Testing
New Transformers
  Manufacturer’s tests
  Utility tests

## Slide 4: What is a CT?
“A current transformer (CT) is used for measurement of alternating electric currents. Current transformers, together with voltage (or potential) transformers (VT or PT), are known as instrument transformers. When current in a circuit is too high to apply directly to measuring instruments, a current transformer produces a reduced current accurately proportional to the current in the circuit, which can be conveniently connected to measuring and recording instruments. A current transformer isolates the measuring instruments from what may be very high voltage in the monitored circuit. Current transformers are commonly used in metering and protective relays in the electrical power industry.” - Wikipedia

## Slide 5: Transformer-Rated
Primarily Commercial/Industrial
(9S, 16S)
Relatively High Current
Example: 400A
400:5
5A

## Slide 6: Current Transformers Conceptual Representation
Real, with core losses
Ideal. No losses

## Slide 7: CT’s – Functions and Terminology
Ratio
For instance, a CT with a 400:5 ratio will produce 5A on the secondary, when 400A are applied to the primary.

## Slide 8: CT’s – Functions and Terminology
Thermal Rating Factor
A value representing the amount by which the primary current can be increased without exceeding the allowable temperature rise.
For instance, a RF of 4.0 at 30° ambient on a 400:5 ratio CT would allow for a primary current up to 1600A.

## Slide 9: CT’s – Functions and Terminology
Accuracy Classifications and Burden
All CT’s fall within an accuracy class.
IEEE Standards have defined accuracy classes.

## Slide 10: CT’s – Functions and Terminology
Accuracy Classifications and Burden
Example: 0.3% @ B0.1, B0.2, B0.5

## Slide 11: CT’s – Functions and Terminology
Faceplate

## Slide 12: Transformer-Rated
9S Meter Installation
5A
PHASE A
SOURCE
PHASE C
PHASE B
LOAD
400A
400A
400A
5A
5A

## Slide 13: Transformer-Rated
9S Meter Installation
5A
PHASE A
SOURCE
PHASE C
PHASE B
LOAD
400A
400A
400A
5A
5A

## Slide 14: Meter Testing
9S Meter Installation
5A
PHASE A
SOURCE
PHASE C
PHASE B
LOAD
400A
400A
400A
5A
5A
Customer Load Meter Test
P
Isolate the Meter
from the Service

## Slide 15: Meter Testing
9S Meter Installation
5A
PHASE A
SOURCE
PHASE C
PHASE B
LOAD
400A
400A
400A
5A
5A
? ? ?

## Slide 16: Meter Testing
9S Meter Installation
5A
PHASE A
SOURCE
PHASE C
PHASE B
LOAD
400A
400A
400A
5A
5A
What if?
355:5
405:5
200:5
Shorted
etc.

## Slide 17: CT Testing
CT Testing is Important!
Test for correct ratio
Test for functionality at rated burdens

## Slide 18: Ratio Testing
Ratio of Primary Current to Secondary Current
5A
PHASE A
SOURCE
LOAD
400A
400A
400A
5A
5A
Calculate Ratio

## Slide 19: Burden Testing
Functionality with Burden Present on the Secondary Loop
PHASE A
Some burden will always be present – junctions, meter coils, test switches, cables, etc.
CT’s must be able to maintain an accurate ratio with burden on the secondary.

## Slide 20: Burden Testing
Functionality with Burden Present on the Secondary Loop

## Slide 21: Burden Testing
Functionality with Burden Present on the Secondary Loop
Example Burden Spec:
0.3% @ B0.1, B0.2, B0.5
or
There should be less than the 0.3% change in secondary current from initial (“0” burden) reading, when up to 0.5Ohms of burden is applied

## Slide 22: Burden Testing
Functionality with Burden Present on the Secondary Loop
ANSI Burden Values
0.1 Ohms
0.2 Ohms
0.5 Ohms
1 Ohms
2 Ohms
4 Ohms
8 Ohms

## Slide 23: Burden Testing
Burden | Reading
0 | 5.0000
0.1 | 4.9999
0.2 | 4.9950
0.5 | 4.9900
1 | 4.9800
2 | 4.9500
4 | 4.0000
8 | 0.8000
0.3% @ B0.1, B0.2, B0.5
Initial Reading = 5Amps
0.3% x 5A = 0.015A
5A – 0.015 = 4.985A

## Slide 24: Burden Testing
Burden | Reading
0 | 5.0000
0.1 | 4.9999
0.2 | 4.9950
0.5 | 4.9900
1 | 4.9800
2 | 4.9500
4 | 4.0000
8 | 0.8000
0.3% @ B0.1, B0.2, B0.5
Initial Reading = 5Amps
0.3% x 5A = 0.015A
5A – 0.015 = 4.985A
At 0.5Ohms of Burden
the secondary current is still at 4.990A – Less than 0.3% change – Good CT!

## Slide 25: Analog Testing
Application of Burden and Calculation
Manual reading of initial and post-burden secondary currents

## Slide 26: Admittance Testing
What is Admittance?
Measured in units of MiliSiemens (mS)
Admittance is the inverse of impedance.
Impedance is the opposition to current.
Therefore, admittance testing measures the overall “health” of the secondary loop of the CT.

## Slide 27: Admittance Testing
Admittance testing devices inject an audio sine wave signal into the secondary loop of the CT.
The resulting current is measured.
The voltage of the initial signal is known.
From these two parameters, the impedance, and thus the admittance can be calculated.

## Slide 28: Admittance Testing
Admittance test results are not immediately intuitive.
Some analysis and interpretation is need.
What do all these mS values mean?

## Slide 29: Admittance Testing
Three phase process is recommended.
Test each CT individually
Test the matched sets
Test over time

## Slide 30: De-magnetization
CT’s can become magnetized, due to a number of reasons, including leaving the shorting clip open, near lightning strikes, and harmonic content.
CT’s can be demagnetized by slowly and smoothly increasing the secondary resistance until saturation occurs, and then slowly and smoothly decreasing the secondary resistance.
A resistance that will cause a secondary current reduction of 65% to 75% will typically put the CT into saturation.

## Slide 31: What We Covered
Why do we test CT’s?
Shop testing
How to read and interpret a transformer face plate
Types of field tests
Magnetization effects and demagnetization

## Slide 32: Questions and Discussion
John Carroll BSc.EE
Western Regional Manager
john.carroll@tescometering.com
TESCO – The Eastern Specialty Company
Bristol, PA
215-228-0500
This presentation can also be found under Meter Conferences and Schools on the TESCO website: tescometering.com
ISO 9001:2015 Certified Quality Company
ISO 17025:2017 Accredited Laboratory