## Slide 1: VAR, VA, and 4 Quadrant Metering
Presented By: Nathaniel Dunn

## Slide 2
1
Power Review
2
VARs & VAs
3
Sources of Reactance
4
Metering W, VAR, VA
5
4 Quadrant Metering
6
Power Quality

## Slide 3: Power Theory Review
Ohm’s Law and Power Calculations

## Slide 4
Ohm’s Law
Ohm’s Law provides basic formulas used for calculating power.
The law states that the current, I, through a conductor is directly proportional to the voltage, E.
The figure to the right provides all the power related formulas derived from Ohm’s Law
Notes: -Defined for DC circuits
?What is difference between DC and AC circuits?
?How is Resistance different/affected in AC circuits?
?How do inductors and capacitors behave in DC circuit?AC circuit?

## Slide 5
Amps
I
Volts
E
Power
P
Ohms (Ω)
R

## Slide 6
In a basic DC circuit, we can use Ohm’s Law to calculate the current for this circuit
Then we can calculate the power consumed by the load
R1 reflects resistant in line from source to load, and R2 is the resistance of the load. In most cases R2 would be much greater than R1. Thus, most of the power is consumed by the load.
These are the same basic applied to metering to measure the power and energy consumed by the load
Basic Circuits

## Slide 7
Inductors similarly are resistive elements in a circuit that don’t have real resistance, but reactance
Like capacitors, in an AC circuit they induce a current into the circuit that affects the phase relationship between voltage and current for that phase
A transformer is an example of an inductor. Most loads have inductive elements/models
Inductive Reactance is defined as;
Inductance
Capacitance
Capacitors are resistive elements in a circuit that don’t have real resistance, but reactance
In AC circuits they create an induced current that affects the phase relationship between voltage and current for that phase
A cap bank is an example of a capacitor
Capacitive Reactance is defined as;
Capacitance and Inductance
DC vs. AC Circuits
Notes: What is the reactance in a DC circuit for a capacitor (infinite)? And, Inductor (0)?

## Slide 8
Capacitors and inductors behave differently in AC circuits compared to DC circuits
In DC circuits a Capacitor will look like an open circuit after fully charging; RC time constant
RC and RL Circuits
DC vs. AC Circuits

## Slide 9
Capacitors and inductors behave differently in AC circuits compared to DC circuits
In DC circuits a Capacitor will look like an open circuit after fully charging; RC time constant
RC and RL Circuits
DC vs. AC Circuits

## Slide 10
Capacitors and inductors behave differently in AC circuits compared to DC circuits
In DC circuits a Capacitor will look like an open circuit after fully charging; RC time constant
Inductors will look like a short circuit after fully charging; 1/RL time constant
RC and RL Circuits
DC vs. AC Circuits

## Slide 11
Capacitors and inductors behave differently in AC circuits compared to DC circuits
In DC circuits a Capacitor will look like an open circuit after fully charging; RC time constant
Inductors will look like a short circuit after fully charging; 1/RL time constant
In AC circuits inductors and capacitors induce a current that causes a phase displacement with the source current. R is replaced with impedance Z;
RC and RL Circuits
DC vs. AC Circuits

## Slide 12
In a capacitive (C) circuit, current (I) leads voltage (V) - ICE
Capacitor – Current leads voltage
Inductor – Voltage leads Current
In inductive (L) circuits, voltage (E) leads current (I) - ELI
ELI the ICE man
How does inductance and capacitance affect AC power?

## Slide 13
+
V
-
R1
R2
Source
Load
+
V
-
R1
R2
Source
Load
C1
+
V
-
R1
R2
Source
Load
L1
+
V
-
R1
R2
Source
Load
+
V
-
Z1=R1+jX1
Source
Load
Z2=R2+jX2

## Slide 14
AC Power Calculations
When calculating AC power you must account for the phase angle difference between the voltage and current signals.
You will notice there are 3 calculations for AC single phase power. We will cover the differences in more detail later
The signals to the left are at unity PF
The base formula of AC power is still;
P = I X E
Notes: What do you notice between voltage, current, and power

## Slide 15
Calculating Energy
A, B, and C are constant in the equation
Energy can be simplified at calculating the area under the curve
High sampling rates provide small distances between data points and reduce error introduce from noise by keeping the line between points flat
Energy is the sum of the area of each section using the trapezoid formula for area
0 0+t 0+2t 0+3t 0+4t a

## Slide 16
Single Phase Power & Energy
Energy accumulation on a sample-by-sample analysis
Energy accumulation accelerates at peaks and decreases at negative peaks
When power wave crosses X axis energy will fall, or have a negative slope
Higher sampling rates provided a more rounded curve, and increase accuracy

## Slide 17
3 Phase Power & Energy (Balanced)
In a balanced 3 phase load, the power total is constant on a sample by sample analysis!
Energy accumulates in a linear progression
This is only true when power is balanced
When power is unbalanced the energy accumulation isn’t linear

## Slide 18: VARs and VAs Calculations
The Power Triangle

## Slide 19
VA stands for Volt-Amps
  VA represents the total demand of a load
  It doesn’t account for phase relationship in calculation, and is determined by the magnitude of voltage and current
VAR stands for Volt-Amps Reactive
  VARs represents the power lost to reactive components, usually as heat.
  VARs are a result of reactive loads like inductors and capacitors
  Calculation for VARs is very similar to calculation for power but uses the sin function instead of cosine.
What are VARs and VAs

## Slide 20
Active power (P) is defined by the following calculation;
Reactive power (Q) is defined by the following calculation;
Apparent power (S) is defined by the following calculation;
And the relationship between all three of these quantities is;
Single Phase Power Calculations

## Slide 21
Trigonomic functions like sine/cosine have a triangular relationship that relates to power
In the AC power calculations, you’ll notice that real power calculation include the cosine function
VARs use the sine function.
When you calculate out the unity circle the cos(x) value also correlates to PF
Cos(0) = 1, and sin(0) = 0, Unity PF
Unity Circle
Understanding Sine/Cosine Relationships

## Slide 22
We’ll also look at some common reference points, and their PF values
30 degrees-
cos(30) = 0.866
sin(30) = 0.5
PF = 86.7%
Unity Circle
Understanding Sine/Cosine Relationships

## Slide 23
We’ll also look at some common reference points, and their PF values
45 degrees-
cos(45) = 0.707
sin(45) = 0.707
PF = 70.7%
Unity Circle
Understanding Sine/Cosine Relationships

## Slide 24
We’ll also look at some common reference points, and their PF values
60 degrees-
cos(60) = 0.5
sin(60) = 0.866
PF = 50%
Unity Circle
Understanding Sine/Cosine Relationships

## Slide 25
We’ll also look at some common reference points, and their PF values
90 degrees-
cos(90) = 0
sin(90) = 1
PF = 0%
Unity Circle
Understanding Sine/Cosine Relationships

## Slide 26
We can populate the rest if the unity circle the same values for every multiple of 30, 45, 60, and 90 degrees
This can be used to quickly identify watt/var relationships and PF at specific points
We calculate the X and Y axis using cosine and sine functions. Similar to calculate watts and vars
Apparent power is also represented in the unity circle by the radius
Unity Circle
Understanding Sine/Cosine Relationships

## Slide 27
(1,0)
(-1,0)
(0,-1)
(0,1)

## Slide 28
579.6
155.4
600

## Slide 29
The unity circle ties directly into the power triangle and 4 quadrant metering
We’re going to calculate power at 15 degrees.
Power Triangle

## Slide 30
The unity circle ties directly into the power triangle and 4 quadrant metering
We’re going to calculate power at 15 degrees.
Cos(15) = 0.966
Sin(15) = 0.259
PF = 96.6%
Power Triangle
0.966
0.259
1

## Slide 31
The unity circle ties directly into the power triangle and 4 quadrant metering
Next, we’ll assume 120 Vrms and 5 Arms
This comes to 600 VA
600 VA * 0.966 = 579.6 W
600 VA * 0.259 = 155.4 VAR
Power Triangle

## Slide 32
Next we’ll use the AC power calculations;
P = 120 * 5 * cos(15) = 579.6 W
Q = 120 * 5 * sin(15) = 155.3 VAR
S = 120 * 5 = 600 VA
PF = P/S = W/VA = 579.6/600 = 0.966
Understanding the unity circle and the mathematical relationship between P, S, and Q will help understanding 4 quadrant metering
Power Calculations

## Slide 33
Power Factor Calculations
Calculation to PF is straight forward, but there are 2 common sign conventions for PF
IEC: Positive Active Power is Positive PF
IEEE: Leading PF is positive, and Lagging is negative

## Slide 34
+Q
(+kVAR, +kVARh)
-Q
(-kVAR, -kVARh)
+P
(+kW, +kWh)
-P
(-kW, -kWh)
Quadrant 1
PF Lagging
Power Factor Sign Convention:
IEEE: -
IEC: +
Quadrant 2
PF Leading
Power Factor Sign Convention:
IEEE: +
IEC: -
Quadrant 3
PF Lagging
Power Factor Sign Convention:
IEEE: -
IEC: -
Quadrant 4
PF Leading
Power Factor Sign Convention:
IEEE: +
IEC: +
Active Power (W)
delivered
Active Power (W)
delivered
Active Power (W)
received
Active Power (W)
received
Reactive Power (VAR)
delivered
Reactive Power (VAR)
received
Reactive Power (VAR)
delivered
Reactive Power (VAR)
received
Apparent Power (VA)
Apparent Power (VA)
Apparent Power (VA)
Apparent Power (VA)
0º
90º
180º
270º

## Slide 36
Most AC loads have some amount of inductance
Transformers are essentially large inductors and major sources of inductive reactance
Cap banks are large capacitors used to offset inductive reactance on the system
Base load power plants like coal, natural gas, and nuclear have good control on power factor output
Transmission lines also have impedance that is directly proportional to the length of the line
Power lines also have some capacitance between earth ground. A capacitor is essentially 2 electrical plates with a dielectric between them, like air.
Source of Reactance

## Slide 37
Any powerline of enough length will generate losses
Longer lines will have greater losses, and see voltage drop
Can calculate impedance from cross sectional area of cable, number of cable, and length
Power Lines

## Slide 38
Power transformers used to step and step down voltage have core and wiring losses associated with them
A power transformer is basically a large inductor and most of the losses are lost as heat and represented as VARs
Transformer losses can be found on the manufacturers test report
Transformers

## Slide 39
Capacitor banks are used for VAR correction and voltage optimization
They’re basically large caps, and are rated in VARs at system frequency
They do consume a small amount of active power as well
Capacitor Banks

## Slide 40
Customer loads will vary from residential to commercial and industrial loads
PF may vary from 85% up to 95%+
Most agreements with large customers have minimum PF requirements
Customers are only billed on Watts, so poor PF is essentially lost revenue
Customer Loads

## Slide 41
Identifying Power from Voltage and Current Signals
What can you tell me about these signals and their power measurements-
P = S
Q = 0
PF = 100% or Unity
Delivered Watts

## Slide 42
Identifying Power from Voltage and Current Signals
What can you tell me about these signals and their power measurements-
Voltage leads Current
Inductive Load
P=Q
Active Power Delivered
Reactive Power Delivered

## Slide 43
Identifying Power from Voltage and Current Signals
What can you tell me about these signals and their power measurements-
Voltage lags Current
Capacitive Load
P=Q
Active Power Delivered
Reactive Power Received

## Slide 44
Identifying Power from Voltage and Current Signals
What can you tell me about these signals and their power measurements-
Current and voltage are 180 degrees apart
P = S
Q = 0
PF = -100% or Unity
Received Watts, -P

## Slide 45
How to measure Phase Shift
Distance from Peak to Peak = 1 cycle
Our electric grid is 60 Hz, or 60 cycles/sec
1 cycle/period = 16.6 ms
V1 peak to I1 peak is phase difference between signals; 1.389 ms
Voltage leads current tells us this is an inductive circuit
The phase angle difference between the two signals is-

## Slide 46
How to measure Phase Shift
PS is the phase shift in degrees
td is time difference
p is period or length of 1 cycle
td and p need to use the same measurement, like seconds or milli-seconds
PS = 360 * (1.389/16.67)
= 30 degrees

## Slide 47
System Overview
Circuit Analysis Point of View

## Slide 48
System Overview
Could looks something like this

## Slide 49
System Overview
Customer Loads
kW tot = 100 MW
kVAR tot = 62 MVAR
kVA tot = 117.65 MVA
Transformer Losses
kW tot = 1 MW
kVAR tot = 10 MVAR
kVA tot = 10.05 MVA
Transformer Losses
kW tot = 1 MW
kVAR tot = 10 MVAR
kVA tot = 10.05 MVA
Line Losses
kW tot = 1 MW
kVAR tot = 2 MVAR
kVA tot = 2.24 MVA
This example doesn’t reflect an actual study
MVA demand from all the loads is 140 MVA
Only 103 MW is billed
VARs are a result of reactive loads on the system that are dispersed as heat
Notes: Using easy math, and not reflecting actual results

## Slide 51
+
V
-
Z1=R1+jX1
Load
Z3=R3+jX3
Z2=R2+jX2

## Slide 52: Metering W, VAR, VA

## Slide 53
So far, we’ve primarily looked at AC power by looking at waveshapes and sampled values
Power meters analyze these values, and calculate the RMS values for each input
  In previous formulas I’ve used RMS values in the power formulas
Meters can provide high speed RMS values; updates several times a second down to half-cycle RMS values
Many meters update once a second and provide RMS and fundamental values;
  RMS values include distortion; sampling rate affects how much distortion is captured
  Fundamental values only account for the 60 Hz signal
Calculating Power

## Slide 54
RMS refers to the root of the average of the squares for a set a data
For our purposes these are the sampled values.
To the right is an example set for a signal that samples at 8 samples/cycle
RMS Values
Root Mean Square of Data Points

## Slide 55
RMS refers to the root of the average of the squares for a set a data
For our purposes these are the sampled values.
To the right is an example set for a signal that samples at 8 samples/cycle
First Step is to square all the sampled values
RMS Values
Root Mean Square of Data Points

## Slide 56
RMS refers to the root of the average of the squares for a set a data
For our purposes these are the sampled values.
To the right is an example set for a signal that samples at 8 samples/cycle
First Step is to square all the sampled values
Then, calculate the average of the squares
RMS Values
Root Mean Square of Data Points

## Slide 57
RMS refers to the root of the average of the squares for a set a data
For our purposes these are the sampled values.
To the right is an example set for a signal that samples at 8 samples/cycle
First Step is to square all the sampled values
Then, calculate the average of the squares
Finally, calculate the square root of the average, of the squares
RMS Values
Root Mean Square of Data Points

## Slide 58
RMS refers to the root of the average of the squares for a set a data
For our purposes these are the sampled values.
To the right is an example set for a signal that samples at 8 samples/cycle
First Step is to square all the sampled values
Then, calculate the average of the squares
Finally, calculate the square root of the average, of the squares
More simply, the RMS value can be calculated by taking the peak and dividing by the square root of 2.
RMS is also the equivalent DC voltage level
RMS Values
Root Mean Square of Data Points

## Slide 59
Calculations for 3 element connected meters
Calculations for 2 element connected meters
3-Phase Power Calculations
Review
+
+
+

## Slide 60
Complex Calculations
  The rectangular form is:
    X indicates the real axis
    jY indicates the imaginary axis
  The polar form is:
    Z indicates magnitude only
    The phase angle (θ) is measured counterclockwise from the positive real axis
  The waveshape form is:
    A indicates the peak magnitude of the signal
    2Ωf is the angular frequency
    t represents time, usually reference to 0
    θ indicates displacement to reference signal in radians

## Slide 61
The previous 3 calculations are all used to calculate correlated values for voltage and current signals
Samples values are used to calculate RMS and phase angle values used in polar coordinates
Polar coordinate and rectangular coordinates represent the same values, but in different forms
  Polar coordinates are ideal for comparing the phasor relationship between voltage and current elements
  Rectangular coordinates are helpful for applying complex math to phasor values
Complex Math
  You can multiply and divide polar coordinate, but cannon add and subtract
  You can add and subtract rectangular values for Net calculations
Complex Values

## Slide 62
Meters today provide real time outputs for;
  Active Power & Energy
  Reactive Power & Energy
  Volt-Amp Power & Energy
  Per phase values for volts, amps, and power
  4 quadrant, bi-directional metering
  And more…!
Data can be collected real time utilizing SCADA, or through data recorders connected to a billing system like MV90
Energy Meter Quantities

## Slide 63: 4 Quadrant Metering

## Slide 64
Power can be broken into 4 quadrants based on direction of active power and reactive power
  +P and +Q is upper right – Quadrant 1
  -P and +Q is upper left – Quadrant 2
  -P and -Q is lower left – Quadrant 3
  +P and -Q is lower right – Quadrant 4
4 Metering Quadrants

## Slide 65
Active energy delivered is Q1+Q4
Power Circle
Quadrant or Quantity

## Slide 66
Active energy delivered is Q1+Q4
Active energy received is Q2+Q3
Power Circle
Quadrant or Quantity

## Slide 67
Active energy delivered is Q1+Q4
Active energy received is Q2+Q3
Reactive energy delivered is Q1+Q2
Power Circle
Quadrant or Quantity

## Slide 68
Active energy delivered is Q1+Q4
Active energy received is Q2+Q3
Reactive energy delivered is Q1+Q2
Reactive energy received is Q3+Q4
Power Circle
Quadrant or Quantity

## Slide 69
-Q
+P
-P
+Q
Quadrant 1
Quadrant 2
Quadrant 3
Quadrant 4
Active Energy Delivered
Active Energy Received
Reactive Energy Delivered
Reactive Energy Received

## Slide 70
Most customer loads will fall into Quadrant 1, from utility perspective
  Active power is delivered to customer
  Most customers will have an inductive impedance which will have reactive power delivered
  Customers with PF correction may have near unity or reactive power received
Bi-directional meters will primarily fall into Q1 and Q3
  Active power delivered and reactive power delivered
  Active power received and reactive power received
Loads in Q2 and Q4 has greater capacitive reactance than inductive, most likely due to PF correction devices
Some generators can output power in Q4 to compensate for low system PF
4 Quadrant Metering

## Slide 71
Configuration 1 captures all active and reactive energy
Configuration 2 captures all active energy, and only reactive energy in inductive quadrants
Configuration 3 captures all active and reactive energy, but splits out reactive energy into quadrants
Preference depends on what power factor correction a customer uses and how to capture it
Channel 1: kWh del
Channel 2: kWh rec
Channel 3: kVARh del
Channel 4: kVARh rec
Channel 1: kWh del
Channel 2: kWh rec
Channel 3: kVARh Q1
Channel 4: kVARh Q3
Channel 1: kWh del
Channel 2: kWh rec
Channel 3: kVARh Q1
Channel 4: kVARh Q2
Channel 5: kVARh Q3
Channel 6: kVARh Q4
Configuration 1
Configuration 3
Configuration 2
4 Quadrant Metering Recorders

## Slide 72: Power Quality

## Slide 73
We’ll focus on Power Factor and Voltage Loss
  Poor PF can increase demand on the system that can’t be recovered
  Lines with significant impedance will see voltage loss over long distances
Corrective devices
  Cap Banks
  Voltage Regulators and Transformer Tap Settings
  Generator and inverter reactive power setpoints
  Static Var Compensators
VVO Software
PF and Voltage Loss

## Slide 74
PF Example
Customer Loads
kW tot = 100 kW
kVAR tot = 62 kVAR
kVA tot = 117.65 kVA
This customer is at 85% PF, and is only billed active energy
Let’s assume $0.10 kWh.
Usage bill at 85% PF would be ~$7.2k
If PF could be increased to 90% PF for month usage bill ~$7.6k
That’s roughly $400 a month or $5k a year
For MW customers the cost will scale by that much!
If you have 100 similar customers that could be $500k a year
Notes: This is a simplified look at costs of PF.

## Slide 75
VA Demand at Generator would be 1800 VA (secondary)
Accounting for power losses (I2 * Z) across system using supplied impedance. VA at customer is 1671.
Current remaining constant, calculate V to be-
VA 111 V
VB 111 V
VC 111 V
Voltage Loss Example
V
V
VA: ??? V
VB: ??? V
VC: ??? V
Z = 10 + j25
A
Notes: This is a simplified look at voltage loss, and using excessive numbers to prove point

## Slide 76: VVO Devices

## Slide 77
Capacitor banks are used for VAR correction and voltage optimization
They’re basically large caps, and are rated in VARs at system frequency
They do consume a small amount of active power as well
Capacitor Banks

## Slide 78
A power distribution voltage regulator is an auto transformer that can step-up or step-down voltage to provide consistent system voltage levels. A voltage regulator control senses system voltage and commands the tap changer to operate when voltage changes are needed.
This can be done with power transformers with multiple tap settings to accomplish the same goal
Voltage Regulator and Transformer Tap Settings

## Slide 79
Generators are capable of operating at leading power factors, but will reduce kVA output
Reactive capability curve provides kVA and kVAR capability at different setpoints
Synchronous generators can be setup as a synchronous condenser to pull VARs off the system
Generator Control

## Slide 80
A static VAR compensator (SVC) is a set of electrical devices for providing fast-acting reactive power on high-voltage electricity transmission networks
The SVC is an automated impedance matching device, designed to bring the system closer to unity power factor. SVCs are used in two main situations:
Connected to the power system, to regulate the transmission voltage ("transmission SVC")
Connected near large industrial loads, to improve power quality ("industrial SVC")
Static VAR Compensator

## Slide 81
Volt/VAR Optimization (VVO) optimally manages system-wide voltage levels and reactive power flow to achieve efficient distribution grid operation.
VVO assists distribution operators reduce system losses, peak demand or energy consumption using Conservation Voltage Reduction (CVR) techniques.
Volt/VAR Optimization Software
Notes: Volt/VAR Optimization & Control is an advanced function that determines the best set of control actions for all voltage regulating devices and Var control devices to achieve a one or more specified operating objectives without violating any of the fundamental operating constraints (high/low voltage limits, load limits, etc.). Volt/VAR Optimization includes Conservative Voltage Reduction (CVR) function that is used to calculate and maintain acceptable voltage (e.g. 120 V +/- 5%) at the service entrance of all customers served by the feeder under all possible operating conditions. CVR is used to flatten voltage profiles and lower overall system voltage while staying within the specified ANSI or IEC voltage limits. Overall system demand can be reduced by a factor of 0.7-1.0% for every 1% reduction in voltage. From a consumers perspective, this reduces the energy they consume. From a utility perspective it reduces the amount of power they need to generate or purchase from a generator.

## Slide 82
Notes: Closing slide