## Slide 1
Hands-On Transformer Rated Polyphase Meter Testing
Presented by John Greenewald, TESCO
and Mike Osterhout, CB & Associates
for MEUA Meter School 102
March 3, 2020
10:45 a.m. – 12:00 p.m.

## Slide 2: Fundamentals of Polyphase Field Meter Testing and Site Verification
The Basics- Differences Between Self Contained and Transformer or Instrument Rated Meter Sites
Transformer Rated Meter Forms
Test Switches and CT’s
Meter Accuracy Testing in the Field
Checking the Health of your CT’s and PT’s
Site Verification

## Slide 3: Fundamentals of Polyphase Field Meter Testing and Site Verification
Typically found in residential metering
Meters are capable of handling the direct incoming amperage
Meter is connected directly to the load being measured
Meter is part of the circuit
When the meter is removed from the socket, power to the customer is interrupted

## Slide 4: Fundamentals of Polyphase Field Meter Testing and Site Verification
Transformer Rated Service
Meter measures scaled down representation of the load.
Scaling is accomplished by the use of external current transformers (CTs) and sometimes voltage transformers or PTs).
The meter is NOT part of the circuit
When the meter is removed from the socket, power to the customer is not effected.

## Slide 5: Fundamentals of Polyphase Field Meter Testing and Site Verification
9S Meter Installation with 400:5 CT’s
400A
400A
400A
LOAD
5A
5A
5A
SOURCE
PHASE A
PHASE B
PHASE C

## Slide 6: Fundamentals of Polyphase Field Meter Testing and Site Verification
Typical Connections for Common Transformer (Instrument) Rated Meter Forms

## Slide 7: Testing at Transformer Rated Sites
Meter Accuracy
Full Load
Light Load
Power Factor
CT Health
Burden Testing
Ratio Testing
Admittance Testing
Site Verification

## Slide 8: TESCO/Georgia Power 2017 Caribbean Meter School Fundamentals of Polyphase Field Meter Testing and Site Verification
Full Load
Light Load
Power Factor
Fundamentals of Polyphase Field Meter Testing and Site Verification
Meter Accuracy Testing in a Nutshell

## Slide 9: The Importance of CT Testing in the Field
One transformer in three wired backwards will give the customer a bill of 1/3rd the actual bill.
One broken wire to a single transformer will give the customer a bill of 2/3rd the actual bill
One dual ratio transformer inappropriately marked in the billing system as 400:5 instead of 800:5 provides a bill that is ½ of the actual bill. And the inverse will give a bill double of what should have been sent. Both are lose-lose situations for the utility.

## Slide 10: The Importance of CT Testing in the Field (continued)
Cross Phasing (wiring errors)
Loose or Corroded Connections
CT Mounted Backwards
CT’s with Shorted Turns
Wrong Selection of Dual Ratio CT
Detect Magnetized CT’s
Burden Failure in Secondary Circuit
Open or Shorted Secondary
Mislabeled CT’s
Ensures all Shorting Blocks have been Removed

## Slide 11: Fundamentals of Polyphase Field Meter Testing and Site Verification
Functionality with Burden Present on the Secondary Loop
PHASE A
Some burden will always be present – junctions, meter coils, test switches, cables, etc.
CT’s must be able to maintain an accurate ratio with burden on the secondary.

## Slide 12: Fundamentals of Polyphase Field Meter Testing and Site Verification
Functionality with Burden Present on the Secondary Loop
Example Burden Spec:
0.3% @ B0.1, B0.2, B0.5
or
There should be less than the 0.3% change in secondary current from initial (“0” burden) reading, when up to 0.5 Ohms of burden is applied
Fundamentals of Polyphase Field Meter Testing and Site Verification

## Slide 13: Fundamentals of Polyphase Field Meter Testing and Site Verification
Functionality with Burden Present on the Secondary Loop
Fundamentals of Polyphase Field Meter Testing and Site Verification
ANSI Burden Values
0.1 Ohms
0.2 Ohms
0.5 Ohms
1 Ohms
2 Ohms
4 Ohms
8 Ohms

## Slide 14: Fundamentals of Polyphase Field Meter Testing and Site Verification
Functionality with Burden Present on the Secondary Loop
0.3% @ B0.1, B0.2, B0.5
Initial Reading = 5Amps
0.3% x 5A = 0.015A
5A – 0.015 = 4.985A
Burden | Reading
0 | 5.0000
0.1 | 4.9999
0.2 | 4.9950
0.5 | 4.9900
1 | 4.9800
2 | 4.9500
4 | 4.0000
8 | 0.8000

## Slide 15: Fundamentals of Polyphase Field Meter Testing and Site Verification
Ratio of Primary Current to Secondary Current
PHASE A
SOURCE
LOAD
400A
400A
400A
5A
5A
Calculate Ratio

## Slide 16: Three Phase Power Blondel’s Theorem
The theory of polyphase watthour metering was first set forth on a scientific basis in 1893 by Andre E. Blondel, engineer and mathematician. His theorem applies to the measurement of real power in a polyphase system of any number of wires. The theorem is as follows:
  - If energy is supplied to any system of conductors through N wires, the total power in the system is given by the algebraic sum of the readings of N wattmeters, so arranged that each of the N wires contains one current coil, the corresponding voltage coil being connected between that wire and some common point. If this common point is on one of the N wires, the measurement may be made by the use of N-1 wattmeters.

## Slide 17: Three Phase Power Blondel’s Theorem
Simply – We can measure the power in a N wire system by measuring the power in N-1 conductors.
For example, in a 4-wire, 3-phase system we need to measure the power in 3 circuits.

## Slide 18: Three Phase Power Blondel’s Theorem
If a meter installation meets Blondel’s Theorem then we will get accurate power measurements under all circumstances.
If a metering system does not meet Blondel’s Theorem then we will only get accurate measurements if certain assumptions are met.

## Slide 19: Blondel’s Theorem
Three wires
Two voltage measurements with one side common to Line 2
Current measurements on lines 1 & 3.
This satisfies Blondel’s Theorem.

## Slide 20: Blondel’s Theorem
Four wires
Two voltage measurements to neutral
Current measurements on lines 1 & 3. How about line 2?
This DOES NOT satisfy Blondel’s Theorem.

## Slide 21: Blondel’s Theorem
In the previous example:
  What are the “ASSUMPTIONS”?
  When do we get errors?
What would the “Right Answer” be?
What did we measure?

## Slide 22: Blondel’s Theorem
Phase B power would be:
  P = Vb Ib cosθ
But we aren’t measuring Vb
What we are measuring is:
  IbVacos(60- θ) + IbVccos(60+ θ)
cos(α + β) = cos(α)cos(β) - sin(α)sin(β)
cos(α - β) = cos(α)cos(β) + sin(α)sin(β)
So

## Slide 23: Blondel’s Theorem
Pb = Ib Va cos(60- θ) + Ib Vc cos(60+ θ)
Applying the trig identity
  IbVa(cos(60)cos(θ) + sin(60)sin(θ))
  IbVc (cos(60)cos(θ) - sin(60)sin(θ))
  Ib(Va+Vc)0.5cos(θ) + Ib(Vc-Va) 0.866sin(θ)
Assuming
  Assume Vb = Va = Vc
  And, they are exactly 120° apart
Pb = Ib(2Vb)(0.5cosθ) = IbVbcosθ

## Slide 24: Blondel’s Theorem
If Va ≠ Vb ≠ Vc then the error is
%Error =
-Ib{(Va+Vc)/(2Vb) - (Va-Vc) 0.866sin(θ)/(Vbcos(θ))
How big is this in reality? If
Va=117, Vb=120, Vc=119, PF=1 then E=-1.67%
Va=117, Vb=116, Vc=119, PF=.866 then E=-1.67%

## Slide 25: Blondel’s Theorem
Condition | % V | % I | Phase A |  |  |  | Phase B |  |  |  | non-Blondel
 | Imb | Imb | V | φvan | I | φian | V | φvbn | I | φibn | % Err
All balanced | 0 | 0 | 120 | 0 | 100 | 0 | 120 | 180 | 100 | 180 | 0.00%
Unbalanced voltages PF=1 | 18% | 0% | 108 | 0 | 100 | 0 | 132 | 180 | 100 | 180 | 0.00%
Unbalanced current PF=1 | 0% | 18% | 120 | 0 | 90 | 0 | 120 | 180 | 110 | 180 | 0.00%
Unbalanced V&I PF=1 | 5% | 18% | 117 | 0 | 90 | 0 | 123 | 180 | 110 | 180 | -0.25%
Unbalanced V&I PF=1 | 8% | 18% | 110 | 0 | 90 | 0 | 120 | 180 | 110 | 180 | -0.43%
Unbalanced V&I PF=1 | 8% | 50% | 110 | 0 | 50 | 0 | 120 | 180 | 100 | 180 | -1.43%
Unbalanced V&I PF=1 | 18% | 40% | 108 | 0 | 75 | 0 | 132 | 180 | 125 | 180 | -2.44%
Unbalanced voltages PF≠1 PFa = PFb | 18% | 0% | 108 | 0 | 100 | 30 | 132 | 180 | 100 | 210 | 0.00%
Unbalanced current PF≠1 PFa = PFb | 0% | 18% | 120 | 0 | 90 | 30 | 120 | 180 | 110 | 210 | 0.00%
Unbalanced V&I PF≠1 PFa = PFb | 18% | 18% | 108 | 0 | 90 | 30 | 132 | 180 | 110 | 210 | -0.99%
Unbalanced V&I PF≠1 PFa = PFb | 18% | 40% | 108 | 0 | 75 | 30 | 132 | 180 | 125 | 210 | -2.44%
Unbalanced voltages PF≠1 PFa ≠ PFb | 18% | 0% | 108 | 0 | 100 | 60 | 132 | 180 | 100 | 210 | -2.61%
Unbalanced current PF≠1 PFa ≠ PFb | 0% | 18% | 120 | 0 | 90 | 60 | 120 | 180 | 110 | 210 | 0.00%
Unbalanced V&I PF≠1 PFa ≠ PFb | 18% | 18% | 108 | 0 | 90 | 60 | 132 | 180 | 110 | 210 | -3.46%
Unbalanced V&I PF≠1 PFa ≠ PFb | 18% | 40% | 108 | 0 | 75 | 60 | 132 | 180 | 125 | 210 | -4.63%
Power Measurements Handbook

## Slide 26: Site Verification: Why should we invest our limited meter service resources here
These customers represent a disproportionately large amount of the overall revenue for every utility in North America.
For some utilities the ten percent of their customers who have transformer rated metering services can represent over 70% of their overall revenue.
While these numbers will vary from utility to utility the basic premise should be the same for all utilities regarding where Meter Services should focus their efforts
This is perhaps one of the larger benefits that AMI can provide for our Utilities – more time to spend on C&I metering and less on residential
Easy Answer: Money.

## Slide 27: Potential list of tasks to be completed during a Site Verification of a Transformer Rated Metering Site
Double check the meter number, the location the test result and the meter record
Perform a visual safety inspection of the site. This includes utility and customer equipment. Things to look for include intact down ground on pole, properly attached enclosure, unwanted voltage on enclosure, proper trimming and site tidiness (absence of discarded seals, etc.)
Visually inspect for energy diversions (intentional and not). This includes broken or missing wires, jumpers, open test switch, unconnected wires and foreign objects on meters or other metering equipment. Broken or missing wires can seriously cause the under measurement of energy. A simple broken wire on a CT or VT can cause the loss of 1/3 to 1/2 of the registration on either 3 element or 2 element metering, respectively.
Visually check lightning arrestors and transformers for damage or leaks.
Check for proper grounding and bonding of metering equipment. Poor grounding and bonding practices may result in inaccurate measurements that go undetected for long periods of time. Implementing a single point ground policy and practice can reduce or eliminate this type of issue.
Burden test CTs and voltage check PTs.

## Slide 28: Site Verification Checklist (continued)
Verify service voltage. Stuck regulator or seasonal capacitor can impact service voltage.
Verify condition of metering control wire. This includes looking for cracks in insulation, broken wires, loose connections, etc.
Confirm we have a Blondel compliant metering set up
Compare the test switch wiring with the wiring at the CTs and VTs. Verify CTs and VTs not cross wired. Be sure CTs are grounded in one location (test switch) only.
Check for bad test switch by examining voltage at the top and bottom of the switch. Also verify amps using amp probe on both sides of the test switch. Verify neutral connection to cabinet (voltage).
Check rotation by closing in one phase at a time at the test switch and observing the phase meter for forward rotation. If forward rotation is not observed measurements may be significantly impacted as the phases are most likely cancelling each other out.
Test meter for accuracy. Verify demand if applicable with observed load. If meter is performing compensation (line and/or transformer losses) the compensation should be verified either through direct testing at the site or by examining recorded pulse data.
Loss compensation is generally a very small percentage of the overall measurement and would not be caught under utilities normal high/low checks. However, the small percentages when applied to large loads or generation can really add up overtime. Billing adjustments can easily be in the $million range if not caught early.

## Slide 29: Site Verification Checklist (continued)
Verify metering vectors. Traditionally this has been done using instruments such as a circuit analyzer. Many solid state meters today can provide vector diagrams along with volt/amp/pf and values using meter manufacturer software or meter displays. Many of these desired values are programmed into the meters Alternate/Utility display. Examining these values can provide much information about the metering integrity. It may also assist in determining if unbalanced loads are present and if CTs are sized properly. The vendor software generally has the ability to capture both diagnostic and vector information electronically. These electronic records should be kept in the meter shop for future comparisons.
If metering is providing pulses/EOI pulse to customers, SCADA systems or other meters for totalization they also should be verified vs. the known load on the meter. If present test/inspect isolation relays/pulse splitters for things like blown fuses to ensure they are operating properly.
Verify meter information including meter multiplier, serial number, dials/decimals, Mp, Ke, Primary Kh, Kr and Rate. Errors in this type of information can also cause a adverse impact on measured/reported values.
Verify CT shunts are all opened.
Look for signs of excessive heat on the meter base e.g.
melted plastic or discoloration related to heat

## Slide 30: Periodic Site Inspections…..
….Can Discover or Prevent:
Billing Errors
Bad Metering set-up
Detect Current Diversion
Identify Potential Safety Issues
Metering Issues (issues not related to meter accuracy)
AMR/AMI Communications Issues
The need for Unscheduled Truck Rolls due to Undetected Field Related Issues
Discrepancies between what is believed to be at a given site versus the actual setup and equipment at the site

## Slide 31: Questions and Discussion
TESCO – The Eastern Specialty Company
Bristol, PA
215-785-2338
This presentation can also be found under Meter Conferences and Schools on the TESCO website: www.tescometering.com