## Slide 1
Verifying
Transformer Rated Service Installations
January 2019

## Slide 2
Field Meter Testing Using
Phantom Load
Notes: These are great test sets, But only test the meter. We would like to test and inspect the complete site

## Slide 3: Opportunity for a problem beyond the meter?
X1
H2
3
0
0
X1
H2
3
0
0
X1
H2
3
0
0
Notes: Lot of opportunities to have something else wrong beside just the meter.

## Slide 4: Instrument Transformers

## Slide 5: Instrument Transformers

## Slide 6: Current Return Switches

## Slide 7: Current Return Switches
C Phase Current in open position

## Slide 8: Current Return Switches
C Phase Current in closed position making contact with attachment screw for shunt buss.
This re-routes current to by pass the meter.

## Slide 9: Current Return Switches

## Slide 10
Form 9S Abase Adaptor
Notes: Inspection of materials that can be bad.

## Slide 11
Nicked Control Cable

## Slide 12: System Analyzers
PowerMetrix
PowerMaster
Spinlab
Bird Dog Plus
testMET
Gold Miner
Radian
RD31-221
Notes: Explain there are many types available
At GPC we have chosen the PowerMaster

## Slide 13: System Analyzer We Use
PowerMaster
5 Series Model

## Slide 14
Testing Options Available
On the PowerMaster
Notes: KWH test with customer load; KVRH test for reactive metering; phantom load; CT burden and/or ratio

## Slide 15
Proper PPE must be worn and all Safety Guidelines followed.
Install the Duckbill Current Leads
Connect the Potential Leads making sure they are matched to the proper current.
Before Beginning the Integrated Site Scan
The Following Steps Must be Performed

## Slide 16
Why ?
Select the Vector Analysis Option
Before Starting
Vector

## Slide 17
View the Vector to Verify your Connections …

## Slide 18
View the Vector to Verify your Connections …

## Slide 19
4 Wire Wye Service at Unity Power Factor

## Slide 20
4 Wire Wye Service at 50% Power Factor

## Slide 21
Single Phase Service
Unity
50% PF
Unity

## Slide 22
No Lag (1.00 PF)
30° Lag (0.866 PF)
Waveform
Three Wire Three Phase Network Service

## Slide 23
Three Wire Three Phase Delta Service
No Lag (1.00 PF)
30° Lag (0.866 PF)

## Slide 24
Delta Service at Unity Power Factor

## Slide 25
Delta Service at 50% Power Factor

## Slide 26: View the Vector to Verify your Connections …

## Slide 27
View the Vector to Verify your Connections …

## Slide 28
View the Vector to Verify your Connections …

## Slide 29
Correct Vector
Potentials and Currents Match.
Start the Scan
What your Looking For!

## Slide 30: Integrated Site Test

## Slide 31
Capture of Sine Waves of Amps & Volts

## Slide 32
Capture of Vector

## Slide 33
Captures System Overall Summary
“Breakdown Of Vector”

## Slide 34
Harmonics for Amp And Volts
Amps
Volts

## Slide 35
Harmonics

## Slide 36: Causes of Harmonics
Harmonics are caused by devices that use an irregular current sinewave when the normal sinewave voltage is applied
LINEAR LOADS (Few Harmonics)
Incandescent Lights
Heating Loads (Resistive)
Some Motors
NON-LINEAR LOADS (Harmonics)
DC Drives
Power Rectifiers
Compact Fluorescent Bulbs

## Slide 37: Harmonic Distortion
Harmonic waveforms are simply multiples of the fundamental waveform.
The graphs below show the relationship between a fundamental (60 Hz) current waveform and a 5th harmonic (300 Hz) component with about 25% peak deviation.
Fundamental (60Hz)
5th Harmonic (300Hz)
Resultant Wave Form

## Slide 38: Incandescent Bulb

## Slide 39: Compact Fluorescent Bulb

## Slide 40: Motor

## Slide 41: Power Supply for Lap Top Computer

## Slide 42
Meter Accuracy Test

## Slide 43
Meter Accuracy Test
Notes: Increase in revolutions under customer load sometimes makes a difference.
Note Elapsed Test Times
Still falls under GPC standards

## Slide 44
Customer or Phantom Load Test

## Slide 45
Meter Accuracy Test Setup
Notes: Discuss number of pulses to using the test time in the Powermate
Three minutes is GPC Standard

## Slide 46
Meter Test Results
kWH

## Slide 47
Phantom Load Tests Results

## Slide 48: Verifying CT Accuracy

## Slide 49: Setup Screen for Verifying CT Accuracy

## Slide 50: Devices Used to Measure the CT’s “Primary” Current (Customer Load)
High Voltage Fiber Optic
Probe
Used on Primary and Overhead
Secondary Services
Flex 36 for Services 600 Volts or Less

## Slide 51: Measuring Secondary Current

## Slide 52: Verifying CT Accuracy on 600 Volts or Less

## Slide 53: Flex Probe Measuring CT’s “Primary” Current in an U.G. Transformer

## Slide 54: Flex Probe Measuring CT’s “Primary” Current in Switchgear
Notes: Stress Importance of getting on the line side of the CTs closest to the transformer

## Slide 55: Important Note Get ahead of the CTs…
Source Side of the CTs
WHY?
Notes: Stress Importance of getting on the line side of the CTs closest to the transformer

## Slide 56
Do your best to get close to the source as possible…
But do it SAFE!

## Slide 57
Fiber Optic Horseshoe Probe used on
Primary Services (above 600 volts)
Notes: Explain “PRIMARY” Current

## Slide 58
Fiber Optic Horseshoe Probe used on
Primary Service (above 600 volts)
Notes: Explain “PRIMARY” Current

## Slide 59
Phase A
125v 1.66a
Phase B
125v 1.60a
Phase C
125v 0.00a
Notes: Explain “PRIMARY” Current

## Slide 60
Fiber Optic Horseshoe Probe used on
Primary Service (above 600 volts)
Notes: Explain “PRIMARY” Current

## Slide 61
Notes: Explain “PRIMARY” Current

## Slide 62
Fiber Optic Horseshoe Probe can also be used on Over Head Secondary Service
Notes: Explain “PRIMARY” Current

## Slide 63
CT Ratio Test Information Results
Possible Errors will be
in RED, this appears to
be a CT running backwards.
If you didn’t check the vector before starting, this is probably your probe installed in
reverse. Check the probe and retest the phase in question.

## Slide 64
CT Ratio Test Information Results

## Slide 65: Results for Ratio Only

## Slide 66
Results for Burden Only

## Slide 67
Should be 2000:5
Ratioed at 1432:5

## Slide 69
Failure Began Before .1 Ohms Of
Burden Is Applied
Bad CT

## Slide 70
Bad CT ?
Ratio Should Be 200 : 5

## Slide 71
No, Just A Bad Electrician
Current Flow
Current Flow
Additional run of wire installed and pulled
through Two CTs backwards

## Slide 72
Bad CT ?
300 : 5 Primary CTs Ratio Results at 112%

## Slide 73
Best Resolution Achieved If Secondary Amps
Are At Least 10% of CT Value
Same CT 15 Minutes Later
What Happened ?
21% of CT
Rated Load
Notes: Earlier Slide CT only had .022% of CT rating where this CT has 21% of CT Load rating

## Slide 74
Vectors
What Do We Look For ?

## Slide 75
Services At Unity Power Factor
4 wire WYE
4 wire Delta
3 wire Delta

## Slide 76
Typical WYE Service

## Slide 77
Problem ?
A Phase and B Phase Current Crossed

## Slide 78
Problem ?
CTs Wired Backwards

## Slide 79
Three Wire Three Phase
Delta Service

## Slide 80
Three Wire Three Phase Delta
Bad Power Factor
15° (Lag)
Normally Leading BY 30 °
Normally Laging BY 30 °
74°
Notes: “C” current would usually be at 270° there is a phase shift of 45° putting the phase angle at 15°
“A” Current would usually be shifted to 30° out of phase with AB potential there is a phase shift of 44° creating an overall phase angle of 74° the result being a .265 power factor.
The combination of the two creates an overall Power Factor of .717

## Slide 81
Three Wire Three Phase Delta
with Worse Power Factor

## Slide 82
Forward Rotation Stops at 90°
as the Angle Increases Reverse Rotation Begins
93°
33°
Three Wire Three Phase Delta
with Even Worse Power Factor

## Slide 83
It looks like A-phase current is matched with B-phase potential, and B-phase current with A-phase potential.
Problem- Crossed Potentials?
Notes: This turned out to be a CT cabinet with two runs of conductor through each CT. On two of the CTs the conductors were not “brothered.”
Phase-C CT was correct. It appeared that an electrician had added another panel at some time after the original installation.

## Slide 84
Instrumentation data from the Metercat Diagnostic Read agreed with data reported from the AMI meter.
As the load changed, the meter would alternate between forward energy flow and reverse energy flow.
Problem- Crossed Potentials?

## Slide 85
The actual problem was found to be non-brothered service conductors through two of the current transformers. Phase-C current transformer on the far right was correct.
B
A
B
A
C
Notes: The meterman had marked the conductors with tape in preparation for correcting the problem, but his A and B phase markings did not match what the meter was seeing as A and B phase due to the conductors on which the meter potential wires were connected. This did not affect getting the problem corrected, but it would have affected our understanding of our vector analysis – therefore the labeling was photo shopped so that our current measurements and vector analysis would make sense.
The conductors marked B-phase were the original conductors feeding the original 400 amp panel. You can see the taped area on the conductor where we originally would have had a split bolt connector for our meter potentials. Someone installed the Utilco connectors and swapped the meter potential wires to the conductors feeding the 225 amp panel that was added. This condition existed when that was done. From other pictures you can see that a #6 bonding wire was added to bond the meter socket. A QA inspection was done here in 2008.

## Slide 86
C-phase CT
Measured 9.5 amps and 49.1 amps

## Slide 87
C-phase CT
Total current measured by C-phase CT was 58.6 amps
Vectors with the same angle simply add together

## Slide 88
Total current measured
Voltage
Current
B
A
C

## Slide 89
A
B
A
B
A-phase CT
Measured 92.3 amps on B-phase and 15.4 amps on A-phase
Notes: The purpose of the next series of slides is to show the current through each conductor compared to the total current measured by the CT and sent to the meter. The CT is summing two currents that have different phase angles. This illustrates that these two currents do not simply add together.

## Slide 90
A-phase CT
Total current measured by A-phase CT was 85.3 amps
How does 92.3 and 15.4 add up to be 85.3 ?

## Slide 91
B-phase CT
Measured 12.5 amps on B-phase and 56.9 amps on A-phase

## Slide 92
B-phase CT
Total current measured by A-phase CT was 47.2 amps
How does 12.5 and 56.9 add up to be 47.2 ?

## Slide 93
Total current measured
Voltage
Current
B
A
C

## Slide 94
A complex number can be visually represented as a pair of numbers (a, b) forming a vector on a diagram, representing the complex plane. "Re" is the real axis, "Im" is the imaginary axis, and i is the imaginary unit

## Slide 95
Illustration of on-site measurements
The customer added the 225 amp panel some time after the original installation.

## Slide 96
Opportunity to Bill for Excessive Reactive Load
Metering Problem ?
Bad Power Factor
Balanced Load

## Slide 97: What can a Customer or Utility do about Bad Factor?

## Slide 98
?
VARs Compensator

## Slide 99
Vars Compensator Off
Vars Compensator On
Site With VARs Compensator Installed
Notes: Some customers have a bad enough Power Factor that they will install a VARs Compensator to get a Power Factor that they will not be penalized for.
Also may help us in the case of an Isolated line out in a rural area that will effect
Residential customers on the line when a load is being pulled.

## Slide 100
SAFETY
IS THE ABSOLUTE NUMBER ONE PRIORITY
Hardhat
·
Eye Protection
·
FR Clothing
·
Rubber gloves with
“Grabbit” gloves or Leather
outer protectors
·