## Slide 1: Site Analysis and Testing for Transformer Rated Service
Looking for Dangerous Installations and Incorrect Billing
Prepared by Tom Lawton, TESCO
The Eastern Specialty Company
For Mississippi State University 43rd Annual Electric Power & Meter School
Tuesday, February 21, 2024 ♦︎ 10:30 AM
Meter II
Notes: 1

## Slide 2: Site Verification: Why should we invest our limited meter service resources here?
These customers represent a disproportionately large amount of the overall revenue for every utility in North America.
For some utilities, the ten percent of their customers who have transformer rated metering services can represent over 70% of their overall revenue.
While these numbers will vary from utility to utility the basic premise should be the same for all utilities regarding where Meter Services should focus their efforts
This is perhaps one of the larger benefits that AMI can provide for our Utilities – more time to spend on C&I metering and less on residential
Easy Answer:

## Slide 3: Potential list of tasks to be completed during a Site Verification of a Transformer Rated Metering Site
Double check the meter number, the location the test result and the meter record
Perform a visual safety inspection of the site. This includes utility and customer equipment. Things to look for include intact down ground on pole, properly attached enclosure, unwanted voltage on enclosure, proper trimming and site tidiness (absence of discarded seals, etc.)
Visually inspect for energy diversions (intentional and not). This includes broken or missing wires, jumpers, open test switch, unconnected wires and foreign objects on meters or other metering equipment. Broken or missing wires can seriously cause the under measurement of energy. A simple broken wire on a CT or VT can cause the loss of 1/3 to 1/2 of the registration on either 3 element or 2 element metering, respectively.

## Slide 4
Visually check lightning arrestors and transformers for damage or leaks.
Check for proper grounding and bonding of metering equipment. Poor grounding and bonding practices may result in inaccurate measurements that go undetected for long periods of time. Implementing a single point ground policy and practice can reduce or eliminate this issue.
Burden test CTs and voltage check PTs.
Verify service voltage. Stuck regulator or seasonal capacitor can impact service voltage.
Verify condition of metering control wire. This includes looking for cracks in insulation, broken wires, loose connections, etc.
Confirm we have a Blondel compliant metering set up
Compare the test switch wiring with the wiring at the CTs and VTs. Verify CTs and VTs not cross wired. Be sure CTs are grounded in one location (test switch) only.
Site Verification Checklist (cont)

## Slide 5: Site Verification Checklist (cont)
Check for bad test switch by examining voltage at the top and bottom of the switch. Also verify amps using amp probe on both sides of the test switch. Verify neutral connection to cabinet (voltage).
Check rotation by closing in one phase at a time at the test switch and observing the phase meter for forward rotation. If forward rotation is not observed measurements may be significantly impacted as the phases are most likely cancelling each other out.

## Slide 6: Site Verification Checklist (cont)
Test meter for accuracy. Verify demand if applicable with observed load. If meter is performing compensation (line and/or transformer losses) the compensation should be verified either through direct testing at the site or by examining recorded pulse data.
Loss compensation is generally a very small percentage of the overall measurement and would not be caught under utilities normal high/low checks. However, the small percentages when applied to large loads or generation can really add up overtime. Billing adjustments can easily be in the $million range if not caught early.

## Slide 7: Site Verification Checklist (cont)
Verify metering vectors. Traditionally this has been done using instruments such as a circuit analyzer. Many solid state meters today can provide vector diagrams along with volt/amp/pf and values using meter manufacturer software or meter displays. Many of these desired values are programmed into the meters Alternate/Utility display. Examining these values can provide much information about the metering integrity. It may also assist in determining if unbalanced loads are present and if CTs are sized properly. The vendor software generally has the ability to capture both diagnostic and vector information electronically. These electronic records should be kept in the meter shop for future comparisons.
If metering is providing pulses/EOI pulse to customers, SCADA systems or other meters for totalization they also should be verified vs. the known load on the meter. If present test/inspect isolation relays/pulse splitters for things like blown fuses to ensure they are operating properly.
Verify meter information including meter multiplier, serial number, dials/decimals, Mp, Ke, Primary Kh, Kr and Rate. Errors in this type of information can also cause a adverse impact on measured/reported values.
Verify CT shunts are all opened.
Look for signs of excessive heat on the meter base e.g.
melted plastic or discoloration related to heat

## Slide 8: Periodic Site Inspections…..
….Can Discover or Prevent:
Billing Errors
Bad Metering set-up
Detect Current Diversion
Identify Potential Safety Issues
Metering Issues (issues not related to meter accuracy)
AMR/AMI Communications Issues
The need for Unscheduled Truck Rolls due to Undetected Field Related Issues
Discrepancies between what is believed to be at a given site versus the actual setup and equipment at the site

## Slide 9: Metering Safety
Fatal Electrical Injuries
The highest rate of fatal electrical injury in 2019 occurred in the Construction industry (0.7/100,000), followed closely by the Utility industry (0.4/100,000).
In 2019, there was one electrical fatality for every 33 fatalities from all causes. The long-term trend has declined from one electrical fatality for each 23 fatalities from all causes in 2003 to the 2019 level of one in 33.

## Slide 10: Does Age Matter – Or Experience?
Fatal Electrical Injuries
In 2019, 8% of all electrical injuries were fatal.
By age group Fatalities tend to go down with age and experience (and perhaps a healthier respect for electricity).
    16 to 17 – 5.4 times as likely as the average worker to experience an electrical injury on the job site.
    18 to 19 years age group – 2.4 times
    20 to 24 years age group - 1.8 times
    25 to 34 years age group - 1.5 times
    35 to 44 years age group – 1.1 times, and;
    those 45 years and up are at or below the average frequency of electrical injury.

## Slide 11: Non-Fatal Electrical Injuries
The median number of days away from work for nonfatal electrical injuries was 9 in 2019.
Electrical injuries are typically classified as burn or shock. For non-fatal injuries, electrical shock injuries were nearly triple the electrical burn injuries in 2019.
The Utility industry rate of nonfatal electrical injury involving days away from work (0.9/10,000) surpassed the Construction industry rate (0.7/10,000) in 2016.
The Mining industry had rate of nonfatal electrical burn injury of 1.0/10,000 for 2016, followed by the Utility industry (0.9) followed by the construction industry (0.4). The rate for all of Private industry remained consistent at 0.1.

## Slide 12: How Dangerous is Metering?
Electricity is Organized Lightning – George Carlin
Any Voltage without current will not kill you, but any voltage with current can kill you.

## Slide 13
How Dangerous is Metering?

## Slide 14: Safety First - PPE
Personal Protective Equipment
Leathers
Rubber Gloves
Face Shield
FR Clothing
Safety Shoes

## Slide 15: Arc Flash
What is Arc Flash?
While an arc flash is sometimes used interchangeably with “arc fault”, an arc flash is more accurately defined as the light produced during an arc fault. An arc fault is a type of electrical fault that results from the breakdown of an insulating medium between two conductors where the energy is sufficient to sustain an arc across the insulator (often air) and can cause extreme amounts of light (arc flash), immense heat upwards of 19,000 degrees C, and a resulting explosive pressure wave (arc blast). These forces combine to create a hazardous condition that can vaporize metal, destroy equipment, and pose a significant hazard to anyone in the vicinity.

## Slide 16: Covering the Basics

## Slide 17: More of the Basics

## Slide 18: How Bad Can Things Get?
Many thanks to Dominion Power
https://youtu.be/2Xoyb9M5-EA
Rubber Gloves and FR 4:10
Meter enclosure – shorted out 10:48
Thanks to Meter Grabber
https://youtu.be/Azuu8VnM36g

## Slide 19: Field Audits, Trouble Shooting and Testing
Always approach an electrical service with caution and while wearing your full PPE. Why?
Never stand directly in front of the meter when removing the meter
Before you even open the box or get the cover off….
  Live box
  Bees
  Other live animals
Broken Seal
Cover dropping off

## Slide 20
Field Audits, Trouble Shooting and Testing 2

## Slide 21: Field Audits, Trouble Shooting and Testing 3

## Slide 22: Once the box is Open: Issues to Look For
Open line – open line side connection to the meter socket.
Missing neutral – missing neutral connection to the center lug in the meter socket
Cross phase condition – cross wiring between the test block and the meter socket.
Hidden jumpers line to load – diversion on both legs.
Dead Short - dead short phase to ground on the load side of one leg of the socket.
Partial Short - partial short phase to ground on the load side of one leg of the socket

## Slide 23: The Importance of CT Testing in the Field (cont)
Cross Phasing (wiring errors)
Loose or Corroded Connections
CT Mounted Backwards
CT’s with Shorted Turns
Wrong Selection of Dual Ratio CT
Detect Magnetized CT’s
Burden Failure in Secondary Circuit
Open or Shorted Secondary
Mislabeled CT’s
Ensures all Shorting Blocks have been Removed

## Slide 24: Testing at Transformer Rated Sites
Meter Accuracy
Full Load
Light Load
Power Factor
CT Health
Burden Testing
Ratio Testing
Admittance Testing
Site Verification

## Slide 25: Backfeed, Ground Fault and other Issues to Look For
Back fed meter socket
Ground fault
Phase to phase fault
Pulling a meter jaw with the meter

## Slide 26
4 Wire Wye Service at Unity Power Factor

## Slide 27
4 Wire Wye Service at 50% Power Factor

## Slide 28: Tools
Socket Pullers
Volt meters
Specialized tools

## Slide 29
Temporary Service Cover
Tools

## Slide 30: Summary
Be Careful
Assume the box is live
Assume there is something live in the box
Treat electricity with respect
Treat all meter boxes with respect

## Slide 31: Around the room
Issues that you may have seen in your metering career already?
Safety Issues not yet brought up?
Closing
Are you not only following the rules but actively making suggestions?

## Slide 32: Most Importantly…
We test and verify the sites to make sure we are not losing money and to make sure the sites are safe.

## Slide 33: Questions and Discussion
Tom Lawton
President
tom.lawton@tescometering.com
TESCO – The Eastern Specialty Company
Bristol, PA
215.228.0500
This presentation can also be found under Meter Conferences and Schools on the TESCO website: tescometering.com
ISO 9001:2015 Certified Quality Company
ISO 17025:2017 Accredited Laboratory