## Slide 1: 21st Century Power Measurements
Prepared by Tom Lawton, TESCO
The Eastern Specialty Company
For Mid-South Meter School
Group 1
Monday, May 1, 2023 at 3:00 PM

## Slide 2: Then – Now – Tomorrow? Meters
First Meters mid-1890s
Westinghouse 1905
2005
2006
2014
2025 ???

## Slide 3: Then – Now – Tomorrow? Meters?

## Slide 4: Then – Now – Tomorrow? Loads
YESTERDAY
TODAY

## Slide 5: Then – Now – Tomorrow? Loads
TODAY

## Slide 6: Then – Now – Tomorrow?
THEN
NOW

## Slide 7: Why do these changes matter?
Changes to our loads have changed the basic computations of metering.
When loads were linear the power triangle was all we needed to know

## Slide 8: Why do these changes matter?
Today’s loads look more like these
Chart: Current for CCFL Light Bulb

## Slide 9: Why do these changes matter?
Today’s loads look more like these
Chart: Variable Speed Motor

## Slide 10: Why do these changes matter?
Today’s loads look more like these
Chart: Current for Switching Power Supply

## Slide 11: Standards Changes
C12.1-2021 American National Standard for Electric Meters—Code for Electricity Metering
  Combines C12.1 and C12.20 into a single modernized document
  Polyphase meters tested using polyphase
  Unbalanced load testing required
  Full harmonic testing required
  Bidirectional energy flow testing required.

## Slide 12: Standards Changes
  Testing with Auxiliary Communications Devices for accuracy required
  Testing for each service type for which the meter is applicable is required
  Blondel vs non-Blondel meter forms and applications are called out.
  An appendix on inherent non-Blondel errors and the governing assumptions is included.
  Many tests were updated to make them more applicable to 21st century applications

## Slide 13: Harmonic Load Waveforms
ANSI C12.1/C12.20 now addresses harmonic waveforms
Chart: 
Chart: 
Chart: 
Chart: 
Chart: 
Chart: Voltage

## Slide 14: Standards Changes
New Revision of C12.10
Safety tests moved here from C12.1
  Much broader safety requirements
  Coordinated effort with UL2735
    Utilities exempt from UL2735 but only if they own and install the equipment

## Slide 15: Standards Changes
Communications Standards
  COSEM has been approved for adoption as an ANSI standard

## Slide 16: ANSI C12.31
There was no non-sinusoidal definition for VA or VAR or Power Factor
New ANSI Standard C12.31 defines these mathematically so every meter manufacturer can use the same calculations
Addresses the issue of non-sinusoidal waveforms
Addresses the issue of polyphase measurements for VA

## Slide 17: ANSI C12.31
RMS Voltage
Basic Definition
Time Domain
Frequency Domain
Waveform

## Slide 18: ANSI C12.31
RMS Current
Basic Definition
Time Domain
Frequency Domain
Waveform

## Slide 19: ANSI C12.31
Active Power
Basic Definition
Time Domain
Frequency Domain

## Slide 20: ANSI C12.31
Apparent Power
Basic Definition
Time Domain
Frequency Domain

## Slide 21: ANSI C12.31
OPEN ISSUE – Polyphase VA
  New approach suggested by John Voisine (Landis+Gyr)
    Tries to better represent VA seen by the transformer
  The issue of how to compute polyphase VA is presently unresolved but is being actively worked on
  The Issue is the meter can neither know the real load configuration nor the transformer configuration

## Slide 22: Next Generation Standards
ANSI C12.46
  New standard in development to eventually replace C12.1-2021
  Structured to be inline with OIML R-46
  New C12.1 has moved much closer to the actual requirements of IR-46.
  Applies to ALL energy measurements
    Watts, VA and VAR
    Uses C12.31 definitions for all quantities

## Slide 23: Next Generation Standards
ANSI C12.46
  Covers ALL waveform types
    sinusoidal, harmonic, time varying
  Defines the meter as everything under the cover
    If there is auxiliary functions in the meter they must be fully operational during accuracy testing
    If an option is added to a meter, the meter must be tested with the option running to remain qualified

## Slide 24: Next Generation Standards
OIML TC12 now working on expanded recommendation
  Expanding to cover VA and VAR
  Adding harmonic performance tests
  Adding new (non-utility) applications
    Sub-metering
    Point of load (Streetlights for example)
    Electric vehicle chargers

## Slide 25: What does the Future Hold?
Traditional meters will have many more integrated features and take on a wider operational role and will become a primary source of system data
Many more devices will have a non-traditional embedded revenue meter
Some will NOT be regulated by the PSC’s

## Slide 26: What does the Future Hold?
The Meter Tech of the future will be
  dealing with these embedded meters
  working with all of these new features
  addressing communications issues
  working across departments at the Utility to provide information and accomplish wider ranging initiatives (e.g. DER)
  Work with a new set of primarily private commercial customers who do not own buildings but own assets piggy backed onto the network

## Slide 27: What about DC?
There are still a number of DC meters out on our systems, primarily in the larger, older urban areas such as San Francisco and New York City.
There has been no effective way to test these legacy meters for some time. This is shortcoming was highlighted as new DC metering applications have begun to make an appearance on the grid and are demanding we find a solution (e.g. DC superchargers)
Using labs with traceable Voltage sources and measurement capabilities and traceable Current sources and measurement capabilities we are now starting to do this.

## Slide 28: DC Theory?
No need for new definitions. Power is simply VA. If we can measure the fundamental Volt and the fundamental Amp then we can create a Standard to measure against and can effectively test our DC meter.

## Slide 29: ANSI C12.32
As always, the theory is only the start. We now need to take this theory and create a practical process. For AC Meters we have been using ANSI C12.1 for many years to guide us on how to move from theory to practice.
We have never had a comparable Standard for DC Metering
ANSI Standard ANSI C12.32 for Electricity Meters for the Measurement of DC Energy has been developed over the past several years and is actively being balloted and is expected to be released in 2022.
This Standard lays out the tests, the definitions, the acceptable performance levels for accuracy as well as functional testing.
Definitions are given and the practical means of type testing as well as acceptance testing are given.

## Slide 30: 2S to 12S to DC Residential?
Are 2S Meters suitable for the need of the residential customer in 2021?
Should we start the transition to all 12S metering for residential if 2S is no longer applicable or desirable?
Should we consider DC metering at the residence and eliminate all inverters other than between the home and grid.
  Should the meter include this inverter?

## Slide 31: Questions and Discussion
Tom Lawton
President
tom.lawton@tescometering.com
TESCO – The Eastern Specialty Company
Bristol, PA
215-228-0500
This presentation can also be found under Meter Conferences and Schools on the TESCO website: tescometering.com
ISO 9001:2015 Certified Quality Company
ISO 17025:2017 Accredited Laboratory