## Slide 1: Introduction to Polyphase Metering
Prepared by Tom Lawton, TESCO
The Eastern Specialty Company
For Mid-South Meter School
Group 2
Wednesday, May 3, 2023 at 10:00 AM
Notes: 1

## Slide 2: 1-Phase and 3-Phase Power
Voltage = Vmax sine 
0 30 60 90 120 150 180 210 240 270 300 330 360
V

## Slide 3: 1-Phase and 3-Phase Power
Forward Rotation, ABC
VA
VC
VB
1200
1200 1200
Volts Phase A Volts Phase B Volts Phase C
0 30 60 90 120 150 180 210 240 270 300 330 360

## Slide 4: The Need for 3-Phase Power
Single-phase motors provide a pulsating torque to a mechanical load. Loads which require more than 10 horsepower generally also require the steadier torque of a 3-phase motor.

## Slide 5: Benefits of 3-Phase Power
Steadier motor torque
Less vibration in machinery
Greater mechanical efficiency
Better voltage regulation
Lower heat losses
Lighter weight conductors

## Slide 6: Network Service & Loads
A-B
B-N
A-N
A
C
B
N
Need to meter line-neutral and line-line loads.
120 V
120 V
208 V

## Slide 7: Network Service & Loads
120 and 208 volt loads
A
B
C
A
B
C
C
N
N
B
A
N
N

## Slide 8: 3-Wire Delta Service & Loads
A-B
C-A
B-C
A-B-C
Need to meter single phase line-line loads, as well as three phase loads.
A
C
B

## Slide 9: 4-Wire Delta Service & Loads
A-N
B-N
B-C
A-B
C-A
A-B-C
A
C
B
N
Need to meter single phase line-neutral and
line-line loads, as well as three phase loads.

## Slide 10: 4-Wire Wye Service & Loads
C-N
A-N
B-N
B-C
A-B
C-A
A
C
B
N
A-B-C
Need to meter single phase line-neutral and
line-line loads, as well as three phase loads.

## Slide 11: Blondel’s Theorem
Blondel says:
If energy is supplied to any system of conductors through N wires, the total power in the system is given by the algebraic sum of readings of N wattmeters, so arranged that each of the N wires contains one current coil, the corresponding potential coil being connected between that wire and some common point. If this common point is on one of the N wires, the measurement may be made by the use of N-1 wattmeters.
Andre E. Blondel, 1893
We would use “watthour meters” in place of “watt meters” and “energy” in place of “power”.
We would also consider “ground” as a possible current carrying conductor when counting “N”.

## Slide 12: Blondel’s Theorem
In a system of N conductors, N-1 meter elements, properly connected, will measure the power or energy taken. The connection must be such that all voltage coils have a common tie to the conductor in which there is no current coil.1
1 From the Handbook For Electricity Metering, 9th edition.

## Slide 13: What is a Meter Form Number?
A Form designation tells us:
  The number and arrangement of meter terminals, and
  The number and internal connection of meter elements (stators).
The Form designation describes the meter, not the service.
  With modern meters, some meter Forms may be used to correctly meter more than one service configuration.
  More than one meter Form could be used with a particular service depending on the connection of the Instrument Transformers.
The same Form designation is usually applicable to equivalent meters of all manufacturers.

## Slide 14: Will’s Meter Forms Cheat Sheet
Consolidated by kV2c Form 16S
Consolidated by kV2c Form 9S
SERVICE | SELF-CONT FORM | XFMR-RATD FORM | NUMBER OF ELEMENTS
1-Phase, 2-W ire | 1S | 3S | 1
1-Phase, 3-W ire | 2S | 4S | 1.5
Network, 3-W ire | 12S | 5S / 45S | 2
3-Phase, 3-W ire, Delta |  |  | 
3-Phase, 4-W ire, Delta | 15S | 8S | 2.5
3-Phase, 4-W ire, Wye | 14S | 6S / 36S | 
 | 16S | 9S | 3
Blondel Solution

## Slide 15: Network, 3-Wire
0
120V
208V
1
120V
2

## Slide 16: Network, 3-Wire

## Slide 17: Network, 3-Wire

## Slide 18: 3-Phase, 3-Wire, Delta
3
A
A
1
A
2
A = 120V, 240V, or 480V

## Slide 19: 3-Phase, 3-Wire, Delta

## Slide 20: 3-Phase, 3-Wire, Delta

## Slide 21: 3-Phase, 4-Wire, Delta
240V
240V
240V
120V
120V
208V
3
1
2
0

## Slide 22: 3-Phase, 4-Wire, Delta

## Slide 23: 3-Phase, 4-Wire, Delta

## Slide 24: 3-Phase, 4-Wire, Wye
N
A
B
VB-N
VA-N
VC-A
V
A-B
VB-C
C
VC-N
Line Voltages (208 or 480V)
Phase Voltages
(120 or 277V)

## Slide 25: 3-Phase, 4-Wire, Wye

## Slide 26: 3-Phase, 4-Wire, Wye

## Slide 27: 3-Phase, 4 Wire, Wye

## Slide 28: 3-Phase, 4-Wire, Wye

## Slide 29: 4-Wire Wye Metering
Form 9
Element,
wire, wye
K Y Z
Form 6
2½ Element, 4 wire, wye
Form 36
2½ Element, 4 wire, wye
K Y
Z
K Y
Z
Transformer-rated

## Slide 30: 4-Wire, Wye Metering
N
K Y Z
C
B
A
9S
Transformer-rated

## Slide 31: 4-Wire, Wye Metering
N
C
B
A
K Y
Z
6S
Transformer-rated

## Slide 32: 4-Wire, Wye Metering
N
C
B
A
36S
Transformer-rated

## Slide 33: 2 Element Meters
Form 5 Form 35 Form 45
Typically used for 3 wire Network or 3 wire, 3 phase Delta applications
Occasionally used for other service types including 2 wire single phase, 4 wire Wye and 4 wire Delta (except Fm 35 not for 4W Delta)
Transformer-rated

## Slide 34: 2 Element Meters
45S
A
LINE
C
LINE
N
LINE
A
LOAD
C
LOAD
N
LOAD
3 wire, network
A
C
B
C
3 wire, delta
A

## Slide 35: Polyphase Meters
Other Considerations
Meter Multipliers
  Self Contained: The meter multiplier is 1
  Transformer Rated: The multiplier is (typically) the product of the CT and VT ratio
Service Types
  Some polyphase meters may be used in multiple service types
Selection
  Proper wiring and form selection is critical

## Slide 36: Polyphase Meters
Select the meter based on the source, not the load.
  The “service type” is not always obvious.
  Loads other than the “known” load can be connected and may be unmetered.
Meter form numbers describe certain meter characteristics not the service or application
Consider that ground can be a current carrying conductor when applying Blondel’s Theorem.
Understand the operation of present day, polyphase solid state meters and how they may be used to advantage

## Slide 37: Combining Polyphase kVAh
kVArh
kVArh
kVArh

## Slide 38: Combining Polyphase kVAh
kVArh
kVArh
kVArh
C
kWh
B
kWh
A
kWh
Vectoral Method (as the crow flies):
 (kWhA + kWhB + kWhC)2 + (kVArhA + kVArhB + kVArhC)2

## Slide 39: Combining Polyphase kVAh
kVArh
kVArh
kVArh
Arithmetic Method:
 kWhA2 + kVArhA2 + kWhB2 + kVArhB2
+ kWhC + kVArhC
2 2

## Slide 40: Combining Polyphase kVAh
kVArh
kVArh
kVArh
C
kWh
B
kWh
A
kWh
Arithmetically combined kVAh > Vectorally combined kVAh They are equal only if all phases have equal phase angles.

## Slide 41: Voltages in a Wye-Connection
VL-L =  3 VL-N
We can prove this by constructing the Line-voltage (L-L) phasors based on the Phase-voltage (L-N) phasors.
1200
0
120 V
A-N
120
0

## Slide 42: Voltages in a Wye-Connection
0
120 V
A-N
120
0
300
1200 300

## Slide 43: Voltages in a Wye-Connection
VA-C VA-N
=
sine 1200 sine 300
VA-C = VA-N sine 1200 / sine 300
VA-C =  3 VA-N
1200
VA-N
Using the Law of Sines:
300
300

## Slide 44: Questions and Discussion
Tom Lawton
tom.lawton@tescometering.com
TESCO – The Eastern Specialty Company
Bristol, PA
215-228-0500
This presentation can also be found under Meter Conferences and Schools on the TESCO website: tescometering.com
ISO 9001:2015 Certified Quality Company
ISO 17025:2017 Accredited Laboratory