## Slide 1: Intro to Self-Contained, Transformer-Rated and Meter Forms
Tuesday, March 8, 2022
9:40 AM – 11:00 AM
Tom Lawton and Rob Reese

## Slide 2: Agenda
Meters 101 - Electro-Mechanical vs Solid-State
Meter Forms
Self-Contained vs Transformer Rated
Blondel’s Theorem
Available References (Hardy’s, UGLY’s Elect Ref)
Examples
1S, 2S, 3S, 4S, 5/35S, 8/9S, 16S

## Slide 3: Meters 101 – Electro-mechanical
Overview of Functionality
The electromechanical induction meter operates through electromagnetic induction
A non-magnetic, but electrically conductive, metal disc which is made to rotate at a speed proportional to the power passing through the meter
The disc is acted upon by two sets of induction coils, which form, in effect, a two phase linear induction motor.
One coil is connected in such a way that it produces a magnetic flux in proportion to the voltage
The other coil produces a magnetic flux in proportion to the current.
The field of the voltage coil is delayed by 90 degrees, due to the coil's inductive nature, and calibrated using a lag coil
This produces eddy currents in the disc and the effect is such that a force is exerted on the disc in proportion to the product of the instantaneous current and instantaneous voltage
A permanent magnet acts as an eddy current brake, exerting an opposing force proportional to the speed of rotation of the disc
The equilibrium between these two opposing forces results in the disc rotating at a speed proportional to the power or rate of energy usage
The disc drives a register mechanism which counts revolutions, much like the odometer in a car, in order to render a measurement of the total energy used.
The amount of energy represented by one revolution of the disc is denoted by the symbol Kh which is given in units of watt-hours per revolution.
A Kh of 7.2 is typical. In this example, each full rotation of the disk is equivalent to 7.2Wh of energy.

## Slide 4: Meters 101 – Solid-state
CURRENT TRANSFORMER
POTENTIAL TRANSFORMER
ADC
FILTER
ADC
FILTER
MICRO
PROC
DISPLAY
COMM
PULSE
Overview of Functionality
Potential and Current is scaled down and conditioned with transformers and filters
ADC’s (analog to digital converters) digitize the signals
A micro-processor or DSP executes the calculations
Resulting data is displayed, sent externally via the communication circuits, and used for the calibrated pulse output

## Slide 5: Meter Forms
1S
2S
3S
4S
5S
6S
9S
12S
15S
16S
25S
45S
10S
11S
13S
14S
17S
24S
32S
39S
26S
35S
46S
56S
66S
76S

## Slide 6: Meter Forms

## Slide 7: Meter Forms
1S
2S
3S
4S
5S
6S
9S
12S
15S
16S
25S
45S
10S
11S
13S
14S
17S
24S
32S
39S
26S
35S
46S
56S
66S
76S

## Slide 8: Meter Forms
TRANSFORMER-RATED
1S
2S
3S
4S
5S
6S
9S
12S
15S
16S
25S
45S
10S
11S
13S
14S
17S
24S
32S
39S
26S
35S
46S
56S
66S
76S
7S
8S
29S
36S
SELF-CONTAINED

## Slide 9: Self-Contained Meters
Relatively Low Current
Example: 100A
Primarily Residential

## Slide 10: Self-Contained
Primarily Residential

## Slide 11: Transformer-Rated Meters
Relatively High Current
Example: 4000A
Primarily Commercial/Industrial
Notes: 11

## Slide 12: Transformer-Rated Meters
Primarily Commercial/Industrial

## Slide 13: Diagram Example
References
Power Measurements Handbook, Dr. Bill Hardy
UGLY’s Electrical References
Meterman’s Handbook
Manufacturer’s websites

## Slide 14: Diagram Example
References
Power Measurements Handbook, Dr. Bill Hardy
UGLY’s Electrical References
Meterman’s Handbook
Manufacturer’s websites

## Slide 15: Diagram Example
3 Current Coils
3 Potential Coils

## Slide 16: Blondel’s Theorem
French Electrical Engineer Andre Blondel
Attempt to simplify electrical measurements and validation of the results
Paper submitted to the International Electric Congress in Chicago in 1893.
E = n - 1
The theorem states that the power provided to a system of N conductors is equal to the algebraic sum of the power measured by N watt-meters. The N watt-meters are separately connected such that each one measures the current level in one of the N conductors and the potential level between that conductor and a common point. In a further simplification, if that common point is located on one of the conductors, that conductor's meter can be removed and only N-1 meters are required.

## Slide 17: Blondel’s Theorem
E = n - 1
The theorem states that the power provided to a system of N conductors is equal to the algebraic sum of the power measured by N watt-meters. The N watt-meters are separately connected such that each one measures the current level in one of the N conductors and the potential level between that conductor and a common point. In a further simplification, if that common point is located on one of the conductors, that conductor's meter can be removed and only N-1 meters are required.
1S
12S
9S
Blondel Compliant

## Slide 18: Blondel’s Theorem
E = n - 1
The theorem states that the power provided to a system of N conductors is equal to the algebraic sum of the power measured by N watt-meters. The N watt-meters are separately connected such that each one measures the current level in one of the N conductors and the potential level between that conductor and a common point. In a further simplification, if that common point is located on one of the conductors, that conductor's meter can be removed and only N-1 meters are required.
2S
Non-Blondel Compliant

## Slide 19: Blondel’s Theorem
Why is non-Blondel metering bad?
Makes assumptions about the service
Example: balanced voltages
Assumptions might not be true
When these assumptions are not true, then there are power measurement errors even if the meter is working perfectly.
The theorem states that the power provided to a system of N conductors is equal to the algebraic sum of the power measured by N watt-meters. The N watt-meters are separately connected such that each one measures the current level in one of the N conductors and the potential level between that conductor and a common point. In a further simplification, if that common point is located on one of the conductors, that conductor's meter can be removed and only N-1 meters are required.

## Slide 20: Blondel’s Theorem
Why are non-Blondel meters used?
Fewer elements (meters) = lower cost
Especially true for electro-mechanical meters
Fewer CT’s and PT’s = lower cost
Less wiring and cheaper sockets
The theorem states that the power provided to a system of N conductors is equal to the algebraic sum of the power measured by N watt-meters. The N watt-meters are separately connected such that each one measures the current level in one of the N conductors and the potential level between that conductor and a common point. In a further simplification, if that common point is located on one of the conductors, that conductor's meter can be removed and only N-1 meters are required.

## Slide 21: Metering Examples

## Slide 22: Metering Examples

## Slide 23: Metering Examples

## Slide 24: Metering Examples

## Slide 25: Metering Examples

## Slide 26: References
https://en.wikipedia.org/wiki/Blondel%27s_theorem
http://www.powermeasurements.org/library/Presentations/NCMS%202013%20-%20Non-Blondel%20Metering.pdf
https://www.baycitymetering.com/

## Slide 27: Questions and Discussion
TESCO – The Eastern Specialty Company
Bristol, PA
215-228-0500
This presentation can also be found under Meter Conferences and Schools on the TESCO website: tescometering.com
ISO 9001:2015 Certified Quality Company
ISO 17025:2017 Accredited Laboratory
Tom Lawton
President
tom.lawton@tescometering.com
Rob Reese
Midwest Regional Sales Manager
rob.reese@tescometering.com