## Slide 1: Caribbean Meter School
January 29, 2019
Atlanta, GA
Fundamentals of Transformer Rated Field Meter Testing and Site Verification
John Greenewald, TESCO

## Slide 2
Purpose:
To acquaint the attendees with the use and purpose of Meter Test Switches
Course Breakdown of Topics:
Using Test Switches
Meter Test Switch Specifications
Meter Test Switch Configurations
Meter Test Switch Accessories
Pre-Wired Transformer Rated Enclosures

## Slide 3
Typically found in residential metering
Meters are capable of handling the direct incoming amperage
Meter is connected directly to the load being measured
Meter is part of the circuit
When the meter is removed from the socket, power to the customer is interrupted
Typical Self Contained Service

## Slide 4
Meter measures scaled down representation of the load.
Scaling is accomplished by the use of external current transformers (CTs) and sometimes voltage transformers or PTs).
The meter is NOT part of the circuit
When the meter is removed from the socket, power to the customer is not effected.
Transformer Rated Service

## Slide 5
Transformer Rated Service
5A
PHASE A
SOURCE
PHASE C
PHASE B
LOAD
400A
400A
400A
5A
5A
5A
5A
5A
9S Meter Installation with 400:5 CT’s

## Slide 6
Testing current transformers while they are in service can be a dangerous operation if certain safety procedures are not followed. The secondary loop of a current transformer must NEVER BE OPENED when service current is present in the primary. When there is current in the primary, and the secondary of a current transformer is open circuited, the voltage across the secondary can rise to hundreds and even thousands of volts, creating an extremely dangerous situation. The open CT secondary voltage magnitude varies with CT design and primary
current flow. The high voltage that is present on the open secondary of an energized current transformer generates two great hazards. The first hazard is ELECTRICAL SHOCK TO TESTING PERSONNEL. The second hazard is THE BREAKDOWN OF THE CURRENT TRANSFORMER INSULATION. Both hazards can be avoided provided that the secondary of the current transformer is never opened. The safest current transformer installations for testing are those that have a Test Switch as part of the secondary loop. A Test Switch is a device that will facilitate inserting instrumentation in the current transformer secondary loop without the danger of opening the circuit.
SAFETY

## Slide 7
Typical Connections for Common Meter Forms

## Slide 8
Test Switch Specifications
ANSI C12 Definitions
Test Switch Materials
Plating
Barriers
Wiring Connections
What to look for
Covers

## Slide 9: ANSI C12.9 Test Switch Definitions

## Slide 10
ANSI C12.9
Test Switches

## Slide 11
ANSI C12.9 General Test Switch Specifications

## Slide 12
Test Switch Configurations
Layout
Handle Colors
Reversed vs. Normal Potentials
Current Links
Base Sizing
Barrier Locations

## Slide 13
Test Switch Accessories
Test Plugs
Safety Covers
Test Switch Isolators
On installations that contain Test Switches, test leads terminated with a test switch
safety test probe (test plug) should be used for CT testing. This provides a “make-before-break” connection to prevent accidental opening of the current transformer secondary loop.

## Slide 14
ANSI C12.9 Test Jack Specifications

## Slide 15
ANSI C12.9 Test Plug Specifications

## Slide 16: For Utilities not Currently Using Test Switches

## Slide 17
Pre-Wired Transformer Rated Enclosures
Cover Types
Wiring
Sockets

## Slide 18
Questions?