## Slide 1: Advanced Polyphase Metering
Presented by John Kretzschmar
June 20, 2017

## Slide 2: Then – Now – Tomorrow? Meters
First Meters mid-1990s
Westinghouse 1905
2005
2006
2014
2025 ???

## Slide 3: Then – Now – Tomorrow? Loads
YESTERDAY
TODAY

## Slide 4: Then – Now – Tomorrow? Loads
TODAY

## Slide 5: Then – Now – Tomorrow? Communications
THEN
NOW

## Slide 6: Why Do These Changes Matter?
Changes to our loads have changed the basic computations of metering
When loads were linear the power triangle was all we needed to know

## Slide 7: Why Do These Changes Matter?
Today’s loads look more like these
Chart: Current for CCFL Light Bulb

## Slide 8: Why Do These Changes Matter?
Today’s loads look more like these
Chart: Variable Speed Motor

## Slide 9: Why Do These Changes Matter?
Today’s loads look more like these
Chart: Current for Switching Power Supply

## Slide 10: Three Phase Power Introduction
Basic Assumptions
Three AC voltage sources
Voltages Displaced in time
Each sinusoidal
Identical in Amplitude

## Slide 11: AC Theory – Sine Wave

## Slide 12: Three Phase Theory Single Phase - Voltage Plot
Chart: PHASE ANGLE
ONE CYCLE
Van

## Slide 13: Three Phase Theory Two Phases - Voltage Plot
Chart: PHASE ANGLE
ONE CYCLE
Van
Vbn

## Slide 14: Three Phase Theory Three Phase - Voltage Plot
Chart: PHASE ANGLE
ONE CYCLE
Van
Vbn
Vcn

## Slide 15: Three Phase Power At the Generator
Chart: PHASE ANGLE
Three voltage vectors each separated by 120°.
Peak voltages essentially equal.
Most of what makes three phase systems seem complex is what we do to this simple picture in the delivery system and loads.
Vcn
Van
Vbn

## Slide 16: Three Phase Power Basic Concept – Phase Rotation
Van
Vbn
Vcn
Phase Rotation:
The order in which the phases reach peak voltage.
There are only two possible sequences:
A-B-C (previous slide)
C-B-A (this slide)
Phase rotation is important because the direction of rotation of a three phase motor is determined by the phase order.

## Slide 17: AC Theory - Phase

## Slide 18: Three Phase Theory Phasors and Vector Notation
Chart: PHASE ANGLE
0
270
90
180
Phasors are a graphical means of representing the amplitude and phase relationships of voltages and currents.
V = sin(θ)

## Slide 19: Three Phase Power Phasors and Vector Notation
0
270
90
180
As stated in the Handbook of Electricity Metering, by common consent, counterclockwise phase rotation has been chosen for general use in phasor diagrams.
Chart: PHASE ANGLE
V = V0sin(θ-120)

## Slide 20: Three Phase Power Phasors and Vector Notation
0
270
90
180
The phasor diagram for a simple 3-phase system has three voltage phasors equally spaced at 120° intervals.
Going clockwise the order is A – B – C.
Chart: PHASE ANGLE
V = V0sin(θ-240)

## Slide 21: Three Phase Theory Symbols and Conventions
Systems formed by interconnecting secondaries of 3 single phase transformers.
Generally primaries are not show unless details of actual transformer are being discussed.

## Slide 22: Three Phase Theory Symbols and Conventions
Often even the coils are not shown but are replaced by simple line drawings

## Slide 23: 3 Phase, 4-Wire “Y” Service 0° = Unity Power Factor
Three Voltage Phasors
120° Apart
Three Current Phasors
Aligned with Voltage at PF=1

## Slide 24: Symbols and Conventions Labeling
Voltages are generally labeled Va, Vb, Vc, Vn for the three phases and neutral
This can be confusing in complex cases
The recommended approach is to use two subscripts so the two points between which the voltage is measured are unambiguous
Vab means voltage at “a” as measured relative to “b”.

## Slide 25: 2 Phase, 3-Wire “Y” Service “Network Connection”
Single phase variant of the service.
Two voltage sources with their returns connected to a common point.
Provides 208 rather than 240 volts across “high side” wires.

## Slide 26: 2 Phase, 3-Wire “Network” Service
Two Voltage Phasors
120° Apart
Two Current Phasors
Aligned with Voltage at PF=1

## Slide 27: 3 Phase, 3-Wire Delta Service
Common service type for industrial customers. This service has NO neutral.
Voltages normally measured relative to phase B.
Voltage and current vectors do not align.
Service is provided even when a phase is grounded.

## Slide 28: 3 Phase, 3-Wire Delta Service Resistive Loads
Two Voltage Phasors
60° Apart
Two Current Phasors
For a resistive load one current leads by 30° while the other lags by 30°

## Slide 29: 3 Phase, 3-Wire Delta Service Resistive Load
Two Voltage Phasors
60° Apart
Two Current Phasors
For a resistive load one current leads by 30° while the other lags by 30°

## Slide 30: 3 Phase, 4-Wire Delta Service
Common service type for industrial customers. Provides a residential like 120/240 service (lighting service) single phase 208 (high side) and even 3 phase 240 V.
Voltage phasors form a “T” 90° apart
Currents are at 120° spacing
In 120/120/208 form only the “hot” (208) leg has its voltage and current vectors aligned.

## Slide 31: 3 Phase, 4-Wire Delta Service Resistive Load
Three Voltage Phasors
90° Apart
Three Current Phasors
120° apart

## Slide 32: AC Theory – Resistive Load
Resistors are measured in Ohms. When an AC voltage is applied to a resistor, the current is in phase. A resistive load is considered a “linear” load because when the voltage is sinusoidal the current is also sinusoidal.

## Slide 33: AC Theory – Inductive Load
Inductors are measured in Henries. When an AC voltage is applied to an inductor, the current is 90 degrees out of phase. We say the current “lags” the voltage. A inductive load is considered a “linear” load because when the voltage is sinusoidal the current is also sinusoidal.

## Slide 34: AC Theory – Capacitive Load
Capacitors are measured in Farads. When an AC voltage is applied to a capacitor, the current is 90 degrees out of phase. We say the current “leads” the voltage. A capacitive load is considered a “linear” load because when the voltage is sinusoidal the current is sinusoidal.

## Slide 35: AC Theory – Power
Power is defined as: P = VI
Since the voltage and current at every point in time for an AC signal is different, we have to distinguish between instantaneous power and average power. Generally when we say “power” we mean average power.
Average power is only defined over an integral number of cycles.

## Slide 36: Time Out for Trig (Right Triangles)
The Right Triangle:
The Pythagorean theory
c2 = a2 + b2

## Slide 37: AC Theory – Definitions
Inductive Reactance – The inductive opposition in a AC circuit = XL
Capacitive Reactance – The capacitive opposition in a AC circuit = XC
Impedance – Total opposition to the flow of current in an AC circuit which includes resistance, XL and XC.
    Impedance = Z = √ [R2 + (XL – XC)2]
Resistive Loads – Light bulbs, heater, etc
Inductive Loads – Electric motors, fans, air conditioners, etc.
Capacitive Loads – Capacitors used to compensate for inductive loads

## Slide 38: AC Theory – Power Triangle (Sinusoidal Waveforms)
If V = Sin(ωt) and I = Sin(ωt - θ) (the load is linear) then:
Active Power = VICos(θ) Watts
Reactive Power = VISin(θ) VARs
Apparent Power = VI VA
Power Factor = Active/Apparent = Cos(θ)
Watts
VARs
VA

## Slide 39: AC Theory – Active Power (Real Power (kW))
In a circuit that contains only resistance:
  Real Power (kW) = VRMS * IRMS
In a circuit that contains resistance and reactance:
  Real Power (kW) = VRMS * IRMS * COS (θ)

## Slide 40: AC Theory – Apparent Power (kVA)
Kilo-Volt-Amperes (kVA) are the product of Volts and the Total Current which flows because of the voltage.
In a circuit that contains only resistance, KVA (apparent power) is equal to the Real Power (kW).
When reactance is introduced into a circuit, and VRMS and IRMS are measured quantities, then:
kVA = VRMS * IRMS
In a circuit where only Real Power (kW) and Reactive Power (kVAR) are measured quantities, then:
kVA = √(kW2 + kVAR2)

## Slide 41: AC Theory – Reactive Power (kVAR)
Reactive Volt Amperes are the product of the total Volt-Amperes and the Sine of the angle of displacement between Voltage and Current.
Reactive Power (kVAR) = VRMS * IRMS * SIN(θ)
kVAR reduces the efficiency in the distribution system, and is NOT used to deliver active power (kW) to the load.

## Slide 42: AC Theory – Reactive Power (kVAR Analogy)

## Slide 43: AC Theory Instantaneous Power
For a resistive load:

## Slide 44: AC Theory Instantaneous Power
For an inductive load:

## Slide 45: AC Theory Instantaneous Power
For a capacitive load:

## Slide 46: AC Theory – Complex Circuits
Amplitude (Current)
Phase (Current)
VC
V
VL
VC
VR

## Slide 47: AC Theory – Instantaneous Power

## Slide 48: AC Theory – Instantaneous Power
From IEEE1459 instantaneous power can be written in several forms:
Active Power
Reactive Power

## Slide 49: Three Phase Power Blondel’s Theorem
If energy be supplied to any system of conductors through N wires, the total power in the system is given by the algebraic sum of the readings of N wattmeters, so arranged that each of the N wires contains one current coil, the corresponding voltage coil being connected between that wire and some common point. If this common point is on one of the N wires, the measurement may be made by the use of N-1 wattmeters.

## Slide 50: Three Phase Power Blondel’s Theorem
Simply put – We can measure the power in a N wire system by measuring the power in N-1 conductors.
For example, in a 4-wire, 3-phase system we need to measure the power in 3 circuits.

## Slide 51: Three Phase Power Blondel’s Theorem
In practice, Blondel’s Theorem is not strictly adhered to in all applications.
Meter manufacturers have found ways to design meters that allow adequate accuracy without the required number of stators.

## Slide 52: Three Phase Power Blondel’s Theorem
One such meter is the common (form 2S) house meter.
It is a single stator meter that is specifically designed to meter a 3-wire circuit.

## Slide 53: Three Phase Power Blondel’s Theorem
Additionally, other meters may be connected in configurations, which may also provide adequate levels of accuracy without the required number of stators.
These are often referred to as Non-Blondel configurations.

## Slide 54: Three Phase Power Blondel’s Theorem
Why are Non-Blondel circuits challenging?
Makes the assumption that the service voltages are balanced.
The assumption may not be true so there are likely to be measurement errors.

## Slide 55: Three Phase Power Blondel’s Theorem
Why are Non-Blondel meters used?
Fewer elements in the meter means lower meter costs.
Fewer PTs and CTs mean lower installation costs.

## Slide 56: Three Phase Power Blondel’s Theorem
Blondel Compliant

## Slide 57: Three Phase Power Blondel’s Theorem
Non-Blondel Compliant

## Slide 58: Blondel’s Theorem
Three wires
Two voltage measurements with one side common to Line 2
Current measurements on lines 1 & 3.
This satisfies Blondel’s Theorem.

## Slide 59: Blondel’s Theorem
Four wires
Two voltage measurements to neutral
Current measurements are on lines 1 and 3 but not line 2.
This DOES NOT satisfy Blondel’s Theorem.

## Slide 60: Blondel’s Theorem
In the previous example:
  What are the “ASSUMPTIONS”?
  When do we get errors?

## Slide 61: Blondel’s Theorem

## Slide 62: Blondel’s Theorem
Phase B power would be:
    P = VbIbCosθ
But we aren’t measuring Vb
What we are measuring is:
    IbVaCos(60- θ) + IbVcCos(60+ θ)

## Slide 63: Blondel’s Theorem
Pb = IbVaCos(60- θ) + IbVcCos(60+ θ)
Applying the trig identity
  IbVa(Cos(60)Cos(θ) + Sin(60)Sin(θ))
  IbVc (Cos(60)Cos(θ) - Sin(60)Sin(θ))
  Ib(Va+Vc)0.5Cos(θ) + Ib(Vc-Va) 0.866Sin(θ)
Assuming
  Assume Vb = Va = Vc
  And, they are exactly 120° apart
Pb = Ib(2Vb)(0.5Cosθ) = IbVbCosθ

## Slide 64: Blondel’s Theorem
If Va ≠ Vb ≠ Vc then the error is
%Error =
-Ib{(Va+Vc)/(2Vb) - (Va-Vc) 0.866Sin(θ)/(VbCos(θ))
How big is this in reality? If
Va=117, Vb=120, Vc=119, PF=1 then E=-1.67%
Va=117, Vb=116, Vc=119, PF=.866 then E=-1.67%

## Slide 65: AC Theory – Power
Power is defined as: P = VI
Since the voltage and current at every point in time for an AC signal is different, we have to distinguish between instantaneous power and average power.
Generally when we say “power” we mean average power.
Average power is only defined over an integer number of cycles.

## Slide 66: Harmonics Curse of the Modern World
Every thing discussed so far was based on “Linear” loads.
      For linear loads the current is always a simple sine wave. Everything we have discussed is true.
For nearly a century after AC power was in use ALL loads were linear.
Today, many loads are NON-LINEAR.

## Slide 67: Harmonics - Definition
Non-sinusoidal complex waveforms are constructed by “adding” together a series of sine wave frequencies known as “Harmonics.”
Harmonics is the generalized term used to describe the distortion of a sinusoidal waveform by waveforms of different frequencies.

## Slide 68: Harmonic Load Waveform
Eq.# | Quantity | Phase A
1 | V(rms) (Direct Sum) | 100
2 | I(rms) (Direct Sum) | 108
3 | V(rms) (Fourier) | 100
4 | I(rms) (Fourier) | 108
5 | Pa = (∫ V(t)I(t)dt) | 10000
6 | Pb = ½∑VnIncos(θ) | 10000
7 | Q = ½∑VnInsin(θ) | 0.000
8 | Sa = Sqrt(P^2 +Q^2) | 10000
9 | Sb = Vrms*Irms(DS) | 10833
10 | Sc = Vrms*Irms(F) | 10833
13 | PF = Pa/Sa | 1.000
14 | PF = Pb/Sb | 0.923
15 | PF = Pb/Sc | 0.923
V = 100Sin(ωt) I = 100Sin(ωt) + 42Sin(5 ωt)

## Slide 69: Harmonic Load Waveform
Eq.# | Quantity | Phase A
1 | V(rms) (Direct Sum) | 100
2 | I(rms) (Direct Sum) | 108
3 | V(rms) (Fourier) | 100
4 | I(rms) (Fourier) | 108
5 | Pa = (∫ V(t)I(t)dt) | 10000
6 | Pb = ½∑VnIncos(θ) | 10000
7 | Q = ½∑VnInsin(θ) | 0.000
8 | Sa = Sqrt(P^2 +Q^2) | 10000
9 | Sb = Vrms*Irms(DS) | 10833
10 | Sc = Vrms*Irms(F) | 10833
13 | PF = Pa/Sa | 1.000
14 | PF = Pb/Sb | 0.923
15 | PF = Pb/Sc | 0.923
Important things to note:
  Because the voltage is NOT distorted, the harmonic in the current does not contribute to active power.
  It does contribute to the Apparent power.
  Does the Power Triangle hold
  There is considerable disagreement about the definition of various power quantities when harmonics are present.
V = 100Sin(ωt) I = 100Sin(ωt) + 42Sin(5 ωt)

## Slide 70: 3 Phase Power Measurement
We have discussed how to measure and view power quantities (W, VARs, VA) in a single phase case.
How do we combine them in a multi-phase system?
Two common approaches:
      Arithmetic
      Vectorial

## Slide 71: 3 Phase Power Measurement
Arithmetic vs Vectoral
Both a magnitude and a direction must be specified for a vector quantity.
In contrast, a scalar quantity which can be quantified with just a number.
Any number of vector quantities of the same type (i.e., same units) can be combined by basic vector operations.

## Slide 72: 3 Phase Power Measurement
VAR and VA calculations can lead to some strange results:
  If we define
PH | W | Q | VA
A | 100 | 0 | 100
B | 120 | 55 | 132
C | 120 | -55 | 132
Arithmetic VA |  |  | 364
Vector VA |  |  | 340

## Slide 73: 3 Phase Power Measurement
Arithmetic Calculation - Form 6 – 4 Wire Y Site
Voltages and Currents Aligned at 0°

## Slide 74: 3 Phase Power Measurement
Vector Calculation - Form 6 – 4 Wire Y Site
Voltages and Currents Aligned at 0°

## Slide 75: 3 Phase Power Measurement
Arithmetic Calculation - Form 6 – 4 Wire Y Site
Currents All shifted by 30°

## Slide 76: 3 Phase Power Measurement
Vector Calculation - Form 6 – 4 Wire Y Site
Currents All shifted by 30°

## Slide 77
Actual Field Test Case #1: Lots of Clues!

## Slide 78
Phase B & C reversed!
Actual Field Test Case #1: Lots of Clues!

## Slide 79
What is the problem?
There is no problem!
3-Wire Delta load
On a 4-Wire Wye service.
Actual Field Test Case #2

## Slide 80: Standards Changes
New Revision of C12.20 in 2015
  Polyphase meters tested using polyphase
    Recommended 2015, required 2020
  Unbalanced load testing required
  Full harmonic testing required
  0.1% Accuracy Class added
  Specific call out of Non-Blondel applications where C12.20 does not apply
  Detailed requirements and specs for test outputs added

## Slide 81: Standards Changes
New Revision of C12.20 in 2015
  Tighter reference condition performance specifications
  When using polyphase loading meters must be tested in each configuration used

## Slide 82: Standards Changes
New Revision of C12.1 in 2015
  0.5% Accuracy Class added
  Testing required for unbalanced loads
  Testing required under unbalanced conditions
  Tighter reference performance requirements
  Bi-directional energy flow testing
  Extensive update on in-service testing

## Slide 83: Standards Changes
New Revision of C12.10 in 2015
  Accuracy tests moved here from C12.1
  Much broader safety requirements
  Coordinated effort with UL2735
    Utilities exempt from UL2735 but only if they own and install the equipment

## Slide 84: Standards Changes
New Revision of C12.9 in 2014
  Full specifications for test plugs included in standard
    Ensures safe operation between all switches and all plugs
    previously some combinations produced safety hazards
  New barrier requirements between switch elements

## Slide 85: Standards Changes
Communications Standards
  New C12.19 which replaces C12.18 and C12.19 is in ballot process
    Major changes – major controversy has held up approval for two years
    Standard will still not guarantee inter-operability
  C12.23 the “Compliance Testing” standard is nearly complete

## Slide 86: Next Generation Standards
ANSI C12.46
  New standard in development to replace C12.1 and C12.20
  Structured like OIML IR-46
  A true digital age standard
  Applies to ALL energy measurements
    Watts, VA and VAR
    Contains precise definitions for the quantities based on digitally sampled waveforms

## Slide 87: Next Generation Standards
ANSI C12.46
  Covers ALL waveform types
    sinusoidal, harmonic, time varying
  Defines the meter as everything under the cover
    If there is auxiliary functions in the meter they must be fully operational during accuracy testing
    If a option is added to a meter, it must be tested with the option running to remain qualified

## Slide 88: Next Generation Standards
ANSI C12.46
  View of accuracy changes
    Currently changes with respect to reference
    New approach is absolute error
Philosophy of C12.46 – When a meter is claimed to be of a specific accuracy class, for example , AC 0.2%, then it’s accuracy under all commonly occurring conditions should be within ±0.2% maximum error.

## Slide 89: New Energy Definitions
Time Domain
Active Power
Apparent Power
Reactive Power

## Slide 90: New Energy Definitions
Frequency Domain
Active Power
Apparent Power
Reactive Power

## Slide 91: What Does the Future Hold?
Over the next FEW years metering may have a whole new meaning
Do these look like meters to you?

## Slide 92: What Does the Future Hold?
Each has an embedded revenue meter
Each claims ANSI C12.1 compliance
METER

## Slide 93
Questions and Discussion
John Kretzschmar
john@samscometering.com
864-590-2883 (cell)
This presentation can also be found under Meter Conferences and Schools on the TESCO web site:
www.tesco-advent.com