## Slide 1
Street Lights – A New Metering Frontier
Prepared by Tom Lawton, TESCO
The Eastern Specialty Company
For North Carolina Electric Meter School
Emerging Technologies Session
Wednesday, June 27, 2018 at 2:45 p.m.

## Slide 2: Introduction
This presentation will discuss the current usages and challenges for streetlight metering and the latest in testing/qualification of streetlight meters.
Photos: Acuity Brands Lighting

## Slide 3: Streetlight Metering—Why change?
LED’s
LED’s have swept through one industry after another over the past twenty five years. Once LED’s are developed for a particular application they take over that industry in just a few years

## Slide 4: LED’s start to take over
A Better Solution
Better lighting of the pavement surface
Light is better directed so there is less light pollution
Less maintenance
Longer Life
Less energy consumed
Ability to control the lighting load by individual light or bank for
  more suitable use given the location and time of day
  emergency situations

## Slide 5: Streetlight Metering—Intelligent Lighting
Streetlight controls:
  Standard photocell operation
  Advanced controls for holiday lighting, billboards, etc.
  Remote mesh network communications
  Scheduling and dimming (LED Lighting)
Graphic: GE lighting

## Slide 6: Streetlight Metering—Intelligent Lighting
Integration of metrology into streetlighting…
Graphic: 360Logica.com

## Slide 7: Streetlight Metering—Intelligent Lighting
Integration of metrology into streetlighting
  Metrology (metering function) integration into “nodes”
  Combining metrology with remote access gives utilities access to information that they may never have had before.
    Read voltage, current and power factor from each node.
    Determine changes in lighting element faults and poor operation.
    This information can be used to determine lighting outages (and dispatch a service truck automatically).
    Can be used to monitor general outages like
    residential meters are now.

## Slide 8: Streetlight Metering—Intelligent Lighting
Energy metering today:
  .5%, 1%, and 2% metering capabilities are now being quoted
  Qualification and validation documentation very sparse.
  No complete ANSI regulation to guide qualification testing, though a committee has formed and a spec is being developed (C136.50)

## Slide 9: Streetlight Metering—Intelligent Lighting
Energy metering today:
  Without the type of qualification testing that metering groups are used to doing prior to rollout of new vendor equipment or technology, billing usage for these nodes has been rare.

## Slide 10: Streetlight Metering—Intelligent Lighting
Using metrology to do energy metering
  A utility may want to test the accuracy of the nodes and work with local municipalities to determine whether the variance in billing due to metering accuracy could still provide better consistency and more accurate billing than current fixed billing algorithms can provide.

## Slide 11: Streetlight Metering—Applications
Applications
  Single streetlight meter
  Group of single streetlight meters
  Meter for a group of streetlights
  Meter for any pole mounted device

## Slide 12: Streetlight Metering—Challenges
Testing Challenges
  Meter test pulse
    Without this pulse, most nodes only report whole watthours through their communications radios. Testing requires 10,000 Wh (in order to get 5 significant digits – 100.00%). 10,000 Wh at 120V and .25A (typical Light Load value) would take 320 hours

## Slide 13: Streetlight Metering—Challenges
Testing Challenges
  Meter setups
    The setup on each node must be checked to make sure that it is not setup to do any scheduled dimming, or scheduled on/off control, so that the output relay remains on during the testing.
    After testing is complete, the setups should be returned to the factory settings before releasing the node.

## Slide 14: Streetlight Metering—Challenges
Testing Challenges
  Functional / Communication testing
    This testing is going to be quite similar to standard revenue meters, as the communications networks used are either the same, or similar to what you are used to.
    One difference would be that if the utility is using scheduled on/off/dimming, that program will have to be setup or downloaded to the node before releasing for installation.

## Slide 15: Streetlight Metering—Challenges
Testing Challenges
  Conclusions
    Testing of streetlight meter nodes will become far easier and less time consuming when they all include IR meter test pulses.
    The testing will all be more equitable for all manufacturers and users once the ANSI specification is released.
    Relevant testing both for accuracy and functionality can still be done in light of the above; it will just take longer and could be somewhat subjective

## Slide 16: Streetlight Metering—Devices Needed and Testing Required
Products:
Test Boards
Mounting sockets
Transformer Rated applications
Field Test Equipment
Meter Farms
Meter Socket Adapters
Tests:
Manufacturer product
evaluation testing
Accuracy testing
Functional testing
Qualification testing

## Slide 17: Negative Business Case
A large investment by Electric Utilities for less revenue
When the market place wants something there is no wisdom in trying to hold back the flood gates. Embrace and figure out how to not only survive but to thrive.
Smart Poles
Additional Lighting
Controls for the Lighting
Potential new products for Industrial Customers
Potential new products for residential customers

## Slide 18: Questions?
Tom Lawton
TESCO – The Eastern Specialty Company
Bristol, PA
215-785-2338
This presentation can also be found under Meter Conferences and Schools on the TESCO web site: www.tescometering.com