## Slide 1
10/02/2012
Slide 1
Complete Site Testing
Prepared by Tom Lawton, TESCO
The Eastern Specialty Company
For North Carolina Electric Meter School
Management
Wednesday 16, 2021 at 8:00 a.m.
Notes: 1

## Slide 2: Topics we will be covering
Transformer Rated Metering & Forms
Importance of CT Testing
Field Testing & Site Verification
Meter Accuracy Testing
Meter Accuracy Testing in the Field
CT Ratio Tests
Phantom Load, Demagnetization and Admittance Testing
Harmonics determination and effects

## Slide 3: Transformer Rated Metering
Meter measures scaled down representation of the load.
Scaling is accomplished by the use of external current transformers (CTs) and sometimes voltage transformers or PTs).
The meter is NOT part of the circuit
When the meter is removed from the socket, power to the customer is not effected.

## Slide 4: The Basic Components
9S Meter Installation with 400:5 CT’s
400A
400A
400A
LOAD
5A
5A
5A
SOURCE
PHASE A
PHASE B
PHASE C

## Slide 5: Typical Meter Connections
Typical Connections for 3 Phase Common Transformer (Instrument) Rated Meter Forms
Examples :
Form 5s Class 20
Form 6S Class 20
Form 9s Class 20

## Slide 6: The Importance of CT Testing in the Field
One transformer in three wired backwards will give the customer a bill of 1/3rd the actual bill.
One broken wire to a single transformer will give the customer a bill of 2/3rd the actual bill
One dual ratio transformer inappropriately marked in the billing system as 400:5 instead of 800:5 provides a bill that is ½ of the actual bill. And the inverse will give a bill double of what should have been sent. Both are lose-lose situations for the utility.

## Slide 7: The Importance of CT Testing in the Field (continued)
Cross Phasing (wiring errors)
Loose or Corroded Connections
CT Mounted Backwards
CT’s with Shorted Turns
Wrong Selection of Dual Ratio CT
Detect Magnetized CT’s
Burden Failure in Secondary Circuit
Open or Shorted Secondary
Mislabeled CT’s
Ensures all Shorting Blocks have been Removed

## Slide 8: Fundamentals of Polyphase Field Meter Testing and Site Verification
Functionality with Burden Present on the Secondary Loop
Example Burden Spec:
0.3% @ B0.1, B0.2, B0.5
or
There should be less than the 0.3% change in secondary current from initial (“0” burden) reading, when up to 0.5 Ohms of burden is applied
Fundamentals of Polyphase Field Meter Testing and Site Verification

## Slide 9: Fundamentals of Polyphase Field Meter Testing and Site Verification
Functionality with Burden Present on the Secondary Loop
PHASE A
Some burden will always be present – junctions, meter coils, test switches, cables, etc.
CT’s must be able to maintain an accurate ratio with burden on the secondary.

## Slide 10: Fundamentals of Polyphase Field Meter Testing and Site Verification
Functionality with Burden Present on the Secondary Loop
0.3% @ B0.1, B0.2, B0.5
Initial Reading = 5Amps
0.3% x 5A = 0.015A
5A – 0.015 = 4.985A
Burden | Reading
0 | 5.0000
0.1 | 4.9999
0.2 | 4.9950
0.5 | 4.9900
1 | 4.9800
2 | 4.9500
4 | 4.0000
8 | 0.8000

## Slide 11: Fundamentals of Polyphase Field Meter Testing and Site Verification
Ratio of Primary Current to Secondary Current
PHASE A
SOURCE
LOAD
400A
400A
400A
5A
5A
Calculate Ratio
80:1

## Slide 12: Testing at Transformer Rated Sites
Safety walk around site
Check PPE
Check test switch
Tighten any loose connections
Check primary cabinet
Check connections
Thermal scan
Connect field tester

## Slide 13: TESCO/Georgia Power 2017 Caribbean Meter School Fundamentals of Polyphase Field Meter Testing and Site Verification
Full Load
Light Load
Power Factor
Meter Accuracy Testing
Meter Accuracy Testing
Customer Load
Customer Load
Customer Billing
Customer Conditions
Meter Accuracy Testing
Phantom Load

## Slide 14: Meter Accuracy Testing
Meter Accuracy Test using IR Pulse Detection
Make connections from Field Tester to Meter Form
Connect IR Pulse Detector to meter output
Check pulse indictor
Pulse Align if necessary

## Slide 15: Meter Accuracy Testing

## Slide 16: Customer CT Ratio Test with Burden
Make Connections from Field Tester to Primary current phases
Make connections from Field Tester to Secondary test switch
Connect IR Pulse Detector to meter output

## Slide 17: CT Ratio Testing with Burden Added

## Slide 18: Phantom Load Testing
Determine the TA ( Test Amps) from Meter Faceplate
Ensure Safety shorting switch and test jack have been disengaged
Make connections from Field Tester to Meter Form using jumper EZ Clips.
Connect IR Pulse Detector to meter output
Check pulse indictor
Pulse Align if necessary

## Slide 19: Phantom Load Testing

## Slide 20: Demagnetization Testing
Current transformers (CTs) show large errors when they are magnetized by dc current. This error can be reduced after proper demagnetization.
One of the methods to demagnetize the CT is to increase the core flux by increasing its burden. This method enables to restore the nominal precision of the heavily magnetized CT from 2.5% back to 0.2% without interruption of the CT operation.

## Slide 21: Admittance Testing
Admittance is a measure of how easily a circuit or device will allow a current to flow. It is defined as the reciprocal of impedance.
The SI Unit of admittance is the (symbol S)

## Slide 22: Harmonics Testing
Harmonics are integer frequencies often found with non linear loads.
THD=Total Harmonic Distortion
Vthd <5%

## Slide 23: Harmonics Testing-Waveforms
Harmonics are generated as a voltage or current at an integer frequency of the system, produced by the action of non-linear loads such as rectifiers, discharge lighting, or switch mode power supplies.
Harmonic frequencies in the power grid are a frequent cause of power quality problems.

## Slide 24: Harmonics Testing-Waveforms
What is the problem with Harmonics?
HEAT.
Can cause significant damage
Safety Hazard
Poor Power Factor
AMI Mesh Interference
Transformer Overheating
Loss of service
Image courtesy of irinfo.org

## Slide 25: Harmonics Testing-Waveforms
Can we reduce or eliminate Harmonics?
Perhaps not eliminate. But we can reduce their impact.
We live in non linear world of power where harmonics are generated.
Pulse Width Modulation conversion and AC Frequency Drive Motors and Pumps.
Many thousands of todays electrical products have Switch Mode Power Supply devices.

## Slide 26: Harmonics Testing-Waveforms
How can we reduce the impact of harmonics ?
Measure and determine major harmonic condition under customer load.
Assess most significant even & odd harmonics.
Active Harmonic Filtering can reduce most significant index.
Power Factor Correction Capacitor.

## Slide 27: Testing at Transformer Rated Sites
Meter Accuracy
Customer Load
Full Load
Light Load
Power Factor
CT Health
Burden Testing
Ratio Testing
Demagnetization
Admittance Testing
Harmonics Assessment
Site Verification

## Slide 28: Periodic Site Inspections…..
….Can Discover or Prevent:
Billing Errors
Bad Metering set-up
Detect Current Diversion
Identify Potential Safety Issues
Metering Issues (issues not related to meter accuracy)
AMR/AMI Communications Issues
The need for Unscheduled Truck Rolls due to Undetected Field Related Issues
Discrepancies between what is believed to be at a given site versus the actual setup and equipment at the site

## Slide 29: Questions and Discussion
Tom Lawton
President
tom.lawton@tescometering.com
TESCO – The Eastern Specialty Company
Bristol, PA
215-228-0500
This presentation can also be found under Meter Conferences and Schools on the TESCO website: www.tescometering.com
ISO 9001:2015 Certified Quality Company
ISO 17025:2017 Accredited Laboratory