## Slide 1
Theory of AC and DC Meter Testing
Prepared by Bill Hardy, TESCO
For North Carolina Electric Meter School
Polyphase
Wednesday, June 26, 2019 at 3:15 p.m.

## Slide 2: A Little History
1800 Volta
  First electric battery
1830-31 Faraday and Henry
  Changing magnetic field can induce an electric current. Build first very crude electric motors in lab.
1832 Pixii
  First crude generation of an AC current.
1856 Siemens
  First really practical electric motor
1860s Varley, Siemens and Wheatstone
  Each develop electric dynamos (DC Generators).
Notes: Werner von Siemens was a German engineer who developed the modern dynamo and held one of the first US patents on electrical meter. Charles Steinmetz research into hysteresis led to better AC motors and transformers.

## Slide 3: A Little History
1870s
  First electric railroad and street lights in Berlin (DC).
1880
  First electric elevator (DC).
1885-88 Thomson, Ferraris, Tesla
  Each develop AC electric induction motors.
  Tesla is granted a US patent for induction motor in 1888.
1890 Dolivo-Dobrovolsky
  First three phase generator, motor and transformer
Notes: Werner von Siemens was a German engineer who developed the modern dynamo and held one of the first US patents on electrical meter. Charles Steinmetz research into hysteresis led to better AC motors and transformers.

## Slide 4: A Little History
Edison and Westinghouse
  Edison favored DC power distribution, Westinghouse championed AC distribution.
  The first US commercial electric systems were Edison’s DC systems.
First AC system was in 1893 in Redlands, CA. Developed by Almirian Decker it used 10,000 volt, three phase primary distribution.
Siemens, Gauland and Steinmetz were other pioneers.
Notes: Werner von Siemens was a German engineer who developed the modern dynamo and held one of the first US patents on electrical meter. Charles Steinmetz research into hysteresis led to better AC motors and transformers.

## Slide 5: War of the Currents
Thomas Edison
George Westinghouse
Nikola Tesla

## Slide 6: AC Theory - History
By 1900 AC power systems had won the battle for power distribution.
  Transformers allowed more efficient distribution of power over large areas.
  AC motors were cheaper and easier to build.
  AC electric generators were easier to build.

## Slide 7: AC vs DC
Direct Current (DC) – an electric current that flows in one direction.(IEEE100)
Alternating Current (AC) – an electric current that reverses direction at regularly recurring intervals of time. (IEEE100)

## Slide 8: AC Circuits
An AC circuit has three general characteristics
  Value
  Frequency
  Phase
In the US, the household value is 120 Volts with other common voltages being 208, 240, 277 and 480 Volts. The frequency is 60 Hertz (cycles per second).

## Slide 9: AC Theory – Sine Wave

## Slide 10: AC Theory - Phase
Here current LAGS voltage.

## Slide 11: AC vs DC
In DC theory we learned
  Ohm’s Law
    Voltage = Current x Resistance
    V = IR
  Power
    P = I2R = V2/R
For AC we would like the same equations to apply.
  Specifically we want to be able to say that a DC voltage of 10 Volts applied to a resistor of value R produces the same power dissipation as an AC voltage of 10 volts applied to the same resistor.

## Slide 12: AC Theory – RMS
For DC voltage to equal AC voltage we need

## Slide 13: AC Theory - RMS
RMS Value

## Slide 14: AC Theory – RMS
So if we want to have the V in our equation for an AC signal represent the same value as the its DC counterpart we have
By convention in AC theory we refer to VDC as the RMS (Root Mean Squared) voltage.
When we talk about AC values we always mean the RMS value not the peak value unless we say so specifically

## Slide 15: AC vs DC
V = IR
P = VI = I2R = V2/R

## Slide 16: AC Theory – Resistive Load
Resistors are measured in Ohms. When an AC voltage is applied to a resistor, the current is in degrees. A resistive load is considered a “linear” load because when the voltage is sinusoidal the current is sinusoidal.

## Slide 17: AC Theory – Inductive Load
Inductors are measured in Henrys. When an AC voltage is applied to an inductor, the current is 90 degrees out of phase. We say the current “lags” the voltage. A inductive load is considered a “linear” load because when the voltage is sinusoidal the current is sinusoidal.

## Slide 18: AC Theory – Capacitive Load
Capacitors are measured in Farads. When an AC voltage is applied to a capacitor, the current is 90 degrees out of phase. We say the current “leads” the voltage. A capacitive load is considered a “linear” load because when the voltage is sinusoidal the current is sinusoidal.

## Slide 19: AC Theory – Active Power
Active Power is defined as P = VI
Power is a rate, i.e. Energy per unit time.
The Watt is the unit for Power
  1 Watt = 1000 Joules/sec
Since the voltage and current at every point in time for an AC signal is different, we have to distinguish between instantaneous power and average power.
Generally when we say “power” we mean average power.

## Slide 20: AC Theory – Energy
Energy is power integrated over a period of time.
The units of Energy are:
  Watt-Hour (abbreviated Wh)
  Kilowatt-Hour (abbreviated kWh)
A Wh is the total energy consumed when a load draws one Watt for one hour.

## Slide 21: AC Theory – Instantaneous Power
For a resistive load:
P = 11520 Watts

## Slide 22: AC Theory – Instantaneous Power
For an inductive load:
P = 0 Watts

## Slide 23: AC Theory – Instantaneous Power
For an capacitive load:
P = 0 Watts

## Slide 24: AC Theory – Complex Circuits
Impedance – The equivalent to the concept of resistance for an AC circuit. It is also measured in Ohms. Designated by the symbol X.
In AC circuits non-resistive impedance affects both the amplitude and phase of the current.
A resistor R has an impedance which is frequency independent. There is no phase shift.
An inductor has an impedance which is proportional the frequency, XL = 2πfL. The phase is shifted by 90 degrees lagging.
A capacitor has an impedance which is inversely proportional the frequency, XC = 1/2πfC. The phase is shifted by 90 degrees leading.

## Slide 25: AC Theory – Complex Circuits
Amplitude (Current)
Phase (Current)
VC
V
VL
VC
VR

## Slide 26: AC Theory – Instantaneous Power

## Slide 27: Time Out for Trig (Right Triangles)
The Right Triangle:
The Pythagorean theory
c2 = a2 + b2

## Slide 28: AC Theory – Power Triangle (Sinusoidal Waveforms)
If V = sin(ωt) and I = sin(ωt - θ) (and the load is linear)
then
Active Power = VIcos(θ) Watts
Reactive Power = VIsin(θ) VARs
Apparent Power = VI VA
Power Factor = Active/Apparent = cos(θ)
Watts
VARs
VA

## Slide 29: Harmonics Curse of the Modern World
Every thing discussed so far was based on “Linear” loads.
  For linear loads the current is always a simple sine wave. Everything we have discussed is true.
For nearly a century after AC power was in use ALL loads were linear.
Today, many loads are NON-LINEAR.

## Slide 30: Harmonic Load Waveforms
ANSI C12.20 now addresses harmonic waveforms as well as sinusoidal.
Chart: 
Chart: 
Chart: 
Chart: 
Test waveforms being proposed for ANSI C12.20.
Chart: 
Chart: Voltage

## Slide 31: AC Theory - Phasors
An easier way to view AC data

## Slide 32: AC Theory - Phasors
The length of the phasor is proportional to the value of the quantity
The angle of the phasor (by convention phase A is drawn as horizontal) shows the phase of the quantity relative to phase A voltage.
Here the current “lags” the voltage by 30 degrees.

## Slide 33: AC Theory - Phasors
Phasors are particularly useful in poly-phase situations

## Slide 34: New Energy Definitions
At the moment there is no non-sinusoidal definition for VA
New ANSI Standard coming very soon
C12.31

## Slide 35: New Definitions
RMS Voltage
Basic Definition
Time Domain
Frequency Domain
Waveform

## Slide 36: New Definitions
RMS Current
Basic Definition
Time Domain
Frequency Domain
Waveform

## Slide 37: New Definitions
Active Power
Basic Definition
Time Domain
Frequency Domain

## Slide 38: New Definitions
Apparent Power
Basic Definition
Time Domain
Frequency Domain

## Slide 39: Questions and Discussion
Bill Hardy, CTO
TESCO – The Eastern Specialty Company
Bristol, PA
865-279-1090 (cell)
215-785-2338 (office)
This presentation can also be found on the TESCO website: www.tescometering.com