## Slide 1
Hot Socket Detection
Best Practices
Prepared by Tom Lawton
TESCO – The Eastern Specialty Company
For the Pennsylvania Rural Electric Association (PREA)
Tuesday, March 13
1:45 p.m to 2:45 p.m.

## Slide 2
This document provides sensitive information concerning a utility’s practices. TESCO and Landis+Gyr provide this document upon request for utilities to facilitate thoughtful internal discussions and to help utilities discuss hot-socket concerns with local fire departments and answering media inquiries.
DO NOT provide this document directly to the public or media to avoid the contents being misused or taken out of context.
Disclaimer – Sensitive Utility Information

## Slide 3: The Issue
Hot Sockets are not a new phenomenon. Virtually every meter man has pulled a meter with a portion of the meter base around a blade melted and virtually every utility has been called to assist in the investigation of a fire at a meter box.
AMI deployments because of the volume of meters involved put a spot light on this issue.
  What causes a hot socket?
  Are the meters ever the cause of a meter box failure?
  What are the things to look for when inspecting an existing meter installation?
  What are the best practices for handling potential hot sockets?
This presentation will cover the results of our lab investigation into the sources for hot sockets, the development of a fixture to simulate hot sockets, the tests and data gleaned from hot sockets, and a discussion of “best practices” regarding hot sockets.
We will also cover new technology developed and patented by TESCO and L+G to use the meter to sense a hot socket and forward an alarm in near real time to the head end system.

## Slide 4: Why do we know anything about hot sockets?
L+G has been investigating hot sockets and how to make their meters withstand hot socket conditions for longer periods of time so the socket has a greater likelihood of being repaired prior to catastrophic failure.
L+G has also been investigating ways to utilize AMI communication to possibly alert head end systems of hot socket incidences.
TESCO has been fortunate enough to be involved in several meter deployments where we supplied full time and part time meter engineers and project managers to our customer’s AMI deployment teams. In this capacity we have been involved in evaluating hot socket issues and helping to determine an appropriate response to actual or potential hot sockets.
TESCO’s meter lab was contracted to develop a laboratory fixture that would simulate the various features common to most hot sockets found in the field. TESCO was also contracted to develop test protocols, gather data and benchmark various conditions and meters.
TESCO has access to a large number of meters which have been exposed to hot sockets both before and after catastrophic failure as well as a limited number of sockets that were hot sockets and did not yet fail catastrophically.

## Slide 5
National Fire Prevention Association (NFPA) tracks sources of home electrical fires - 2013 report.
No NFPA data 1999-2001
Electrical Fires Generally Decreasing

## Slide 6
610 fires/year in the vicinity of the Meter or Meter Box
Sources of Electrical Fires Annualized Rate of Occurance 2007-2011

## Slide 7
Approximately 141 million connected customers in the United States with approximately 170 Million installed electric meters. Using 610 fires at or near the meter per year yields 3.6 fires per million meters per year without AMI deployments.
Electrical Fires Near the Meter Annualized Rate of Occurance 2007-2011

## Slide 8
Replacing a meter in an existing meter socket will weaken the socket and if performed enough times this action will create a hazardous condition. AMI deployments will increase the incidence of hot sockets and meter fires unless precautionary steps are taken as part of the meter deployment.
Electrical Fires Near the Meter Annualized Rate of Occurance 2007-2011

## Slide 9: Searching for Hot Socket sources
Pitted and discolored meter blades
Melted plastic around one or more of the meter stabs (typically the plastic around one stab is where the deformation starts)
Pitted and discolored socket jaws
Loss of spring tension in the socket jaws
Common Features and Common Sources of Concern

## Slide 10
Sprung/damaged jaw
Loose wire termination at line or load side jaw
Meter blade beside and not into socket jaw
Worn line/load wire insulation arcing over to grounded mounting box
Total load exceeding socket capacity – lots of older 100 amp services in the field
What are Likely Socket Concerns?

## Slide 11
Tin plating on jaw “cooked”
Heat accelerates oxidation on lug wire
Note: Tin Melts at 232ºC (450ºF)
Hot Socket Causes – Sprung Jaws

## Slide 12
Jaw completely separated - large gap resulting in poor connection
Example – “Sprung Jaw”

## Slide 13
Hot Socket Simulation Fixture
Click to view video

## Slide 15: Expected & Unexpected Results
Expected:
Hot Sockets are exactly that – hot sockets. The hot sockets are the source of the problem and not hot meters.
Electromechanical meters withstand hot sockets better than solid state meters
Unexpected:
Current plays only a small role in how quickly a meter will burn up. Meters were burned up nearly as quickly at 3 amps, 30 amps, and 130 amps.
Relatively small amounts of vibration can be the catalyst in the beginning and eventual catastrophic failure of a hot socket. Note: Other catalysts include but are not limited to power surges, debris, humidity, salt water.
Contact resistance plays no role in creating a hot socket
And some newer solid state meters are better than electromechanical meters.
Notes: 15

## Slide 16: Temperature Rise Data

## Slide 17
Jaws with intermittent connections will arc to the meter blade resulting in pitting on the blade.
Blade shows early signs of arcing.
Tin Melts at 232ºC which is lower than the 350ºC base plate plastic.
Jaw to Blade Arcing

## Slide 18
18
Tin burned off
Blade hole due to arcing to jaw – Copper melts at 1040ºC (1984ºF)
AX-SD base thermoset plastic melts at 960ºC (1760ºF)
Severe Arcing Jaw to Blade

## Slide 19: What are the necessary ingredients for a hot socket?
There are three necessary ingredients to create a hot socket (Note: We are not suggesting that we have simulated or even understand all causes for all hot sockets and meter related fires, but rather that we have simulated and understand the causes behind most hot sockets and meter related fires);
  Loss of jaw tension in at least one of the socket jaws.
  Vibration (or other catalyst
  to initiate arcing)
  Minimal load present

## Slide 20: Reviewing the data and learning from the data
Repeated meter insertions degrades the tension in the socket jaws (see graph), but not to dangerous levels
Exposure to elevated temperatures rapidly degrades the socket jaw tension to dangerous levels (see graph)
Visual inspection will catch some but not all dangerous socket jaws
Arcing creates the heat
Exposure to elevated temperatures has a cumulative effect on the meter socket jaw
Relatively small vibration can initiate arcing

## Slide 22: Field Inspection of Sockets Best Practices
Example field check list
  Gaps in meter socket jaws
  Discoloration of one jaw vs. the other three
  Signs of melted or deformed plastic on meter base
  Pitting of either meter blade or socket jaw
  Loss of tension in meter socket jaws
  Check condition of wire insulation and connections to meter jaws
  Check the overall condition of the box, socket, meter and how they attach to each other and the building.
  Look for signs of tampering
  Look for signs of water or debris inside of the meter can

## Slide 23: Who Sees Hot Sockets?
Most AMI deployments utilize third party contractors to handle residential and some self contained non-2S services.
After to or prior to AMI deployments, Utility personnel typically see these sockets
Transformer rated meters typically handled by the meter service department of the utility.
Hot socket concerns with lever by-pass sockets used on 3-phase meters are extremely rare.

## Slide 24: What can be done once a hot socket is identified?
Easiest resolution is to replace the damaged jaw.
Never try and repair a damaged jaw by simply “squeezing” the damaged jaw with a pair of pliers or other tool. The metallurgical properties of the jaw will not magically return and the jaws will simply spread again as soon as a meter is put into the socket.
If the other jaws are deemed to be in good repair, the box and wiring are in good condition and appropriate Socket Blocks are available to effect a repair, then replacing the damaged socket block with a new one is the most expedient and cost effective solution. If any of these conditions do not exist then replacing the box is the best solution.
Notes: 24

## Slide 25: Base Line Data Electro Mechanical meters vs solid state vs the latest generation of meters designed with hot sockets in mind
At the start of our laboratory investigation the oldest electro mechanical meters withstood hot sockets the best
The latest vintage solid state meters withstood hot sockets the least.
Over the course of the past twenty four months virtually every meter manufacturer has begun to release 2S meters designed to withstand hot sockets.

## Slide 26: In Search of Hot Sockets
The meter manufacturer’s and various electric utilities have also been looking at a variety of ways to better sense hot sockets.
Utilities who have deployed are looking for a set of alarms that when taken together may give them a better idea that there is a hot socket
Meter Manufacturers have worked on evaluating a variety of temperature levels to send an alarm, disconnecting the meter if there are sustained elevated temperatures, using increased impedance to signify a hot socket, improving the temperature sensors and putting additional temperature sensors on the blades of the meters.

## Slide 27: Finding a Hot Socket with a meter – What is known and Keys to these new technologies
Temperature Sensing – sensing the temperature at the metrology board and at the meter stab(s)
Impedance Sensing – detecting a change in impedance in the meter circuit
Detecting the RF signature of a micro Arc with a near field sensor - Arcing emits broadband energy in the form of radio waves. Launching radio waves requires a disturbance in the electric and magnetic fields near where the arc occurs (the near-field space).

## Slide 28: Summary of the Problem
Hot sockets start with a loss of tension in at least one of the meter socket jaws. This loss of tension can be from a variety of sources that start as early as improper installation or even “tight sockets”.
Loss of tension is necessary to create the initial micro-arcing conditions.
Sockets with repeated meter exchanges observed to have higher incidence of hot socket issues and “booting” a meter may spring jaws even more.
Vibration appears to be the most common catalyst to the micro-arcing that creates the initial heat in a “hot socket”.
The meter must have some power, but current is not a significant factor in how quickly or dramatically a hot socket occurs
The effects of vibration and weakened jaw are cumulative

## Slide 29: Summary of the Potential Solutions
Meter Manufacturers have all been working on the design of their meters to better withstand a hot socket. These new meters have better baseline performance than even the older electro mechanical meters, but a hot socket will eventually burn up even the most robust meter.
Thorough visual inspections of all services when replacing a meter whether for AMI or not
Hot Socket Indicator inspection for all jaws. This is a non-invasive way to check that the minimum safe holding force or greater is present in all socket jaws.
Hot Socket clips. Allows for the meter tech to leave the service as safe or safer than when the problem jaw has been identified.
In Meter circuit for near real time detection and alarm to the head end allows the utility to identify compromised jaws before they damage the meter and before they become dangerous to the rate payer or tenant.

## Slide 30: Questions and Discussion
Tom Lawton
TESCO – The Eastern Specialty Company
Bristol, PA
215.785.2338
215.688.0298 (cell)
Tom.Lawton@tescometering.com
This presentation can also be found under Meter Conferences and Schools on the TESCO web site: www.tescometering.com