## Slide 1: Intro to Transformer Rated Metering
PREA
March 5, 2024
Rob Reese, TESCO

## Slide 2: Self-Contained vs. Transformer-Rated
1S
2S
3S
4S
5S
6S
9S
12S
15S
16S
25S
45S
10S
11S
13S
14S
17S
24S
32S
39S
26S
35S
46S
56S
66S
76S

## Slide 3: Self-Contained vs. Transformer-Rated
1S
2S
3S
4S
5S
6S
9S
12S
15S
16S
25S
45S
10S
11S
13S
14S
17S
24S
32S
39S
26S
35S
46S
56S
66S
76S
TRANSFORMER RATED
7S
8S
29S
36S
SELF-CONTAINED

## Slide 4: Self-Contained Metering
Relatively Low Current
Example: 100A
Primarily Residential
(1S, 2S, 12S)

## Slide 5: Self-Contained Metering
Primarily Residential
(1S, 2S, 12S)

## Slide 6: Transformer-Rated Metering
Relatively High Current
Example: 2000A
Primarily Commercial/Industrial
(9S)

## Slide 7: Transformer-Rated Metering
Primarily Commercial/Industrial
(9S)

## Slide 8: Transformer-Rated Metering
Typical Components of an Installation

## Slide 9: Transformer-Rated Metering
Meter

## Slide 10: Transformer-Rated Metering
Meter

## Slide 11: Transformer-Rated Metering
Enclosure, Socket, Test Switch

## Slide 12: Transformer-Rated Metering
Enclosure, Socket, Test Switch
Enclosure
Painted Steel or Aluminum
One or Two Piece Lid
Many, Many Configurations

## Slide 13: Transformer-Rated Metering
Enclosure, Socket, Test Switch
Socket
Configured for Specific Form

## Slide 14: Transformer-Rated Metering
Enclosure, Socket, Test Switch
Test Switch
Upmost Safety
Shuts the CT
Isolates the Meter from the Service During Testing

## Slide 15: Transformer-Rated Metering
PT/VT –Voltage Transformer

## Slide 16: Transformer-Rated Metering
PT/VT –Voltage Transformer
PT/VT
Scales Down the Voltage
4:1
480V:120V

## Slide 17: Transformer-Rated Metering
CT – Current Transformer

## Slide 18: Transformer-Rated Metering
CT – Current Transformer
CT
Scales Down the Current
400:5
800A:10A

## Slide 19: Faceplate Specifications

## Slide 20: Faceplate Specifications
Ratio

## Slide 21: Faceplate Specifications
Thermal factor

## Slide 22: CT’s – Functions and Terminology
Thermal Rating factor
A value representing the amount by which the primary current can be increased without exceeding the allowable temperature rise.
For instance, a RF of 4.0 at 30° ambient on a 400:5 ratio CT would allow for a primary current up to 1600A.

## Slide 23: Faceplate Specifications
Accuracy Classifications
All CT’s fall within an accuracy class.
IEEE Standards have defined accuracy classes.

## Slide 24: Faceplate Specifications
BurdenRating

## Slide 25: Burden Rating
.3@B0.1,B0.2
The burden range, present in the secondary circuit, that the manufacturer will guarantee their CT’s will still accurately function, in regards to the ratio specification.

## Slide 26: Questions and Discussion
Rob Reese
Midwest Regional Sales Manager
rob.reese@tescometering.com
TESCO – The Eastern Specialty Company
Bristol, PA
215.310.8809
This presentation can also be found under Meter Conferences and Schools on the TESCO website: tescometering.com
ISO 9001:2015 Certified Quality Company
ISO 17025:2017 Accredited Laboratory